## CWLNG Conditions Raci Matrix
| X = Responsible to provide the documentation S= Discipline is support to Owner | [5 empty] | Owner | PE Stamping & Seal | Commissioning | Construction | HSE Management | QA/QC | Security | Process | Process Safety | HSE Design (Fire fighting) | HSE Design - Noise and Vibration | HSE Design - Environment | Geotechnics | Civil & Structural stick built | Architectural Buildings (stick built) | Modularized Buildings | Module Structural Engineering | Piping Installation | Piping Material | Welding | Materials & corrosion / Painting / insulation | Electrical / Cathodique Protection | Instrumentation Control Systems | Telecom | Packages & Fired Equipment | Rotating Equipment | Pressure Vessels | HVAC for Substation & RIE | HVAC for Architectural buildings | Weight control | Module Transport and Installation | LNG Tank | Marine / Coastal | Regulatory Compliance | Planning | Project Management | Cyber | Advanced Systems Engineering (ASE) | Project Execution System (PES) | Project Document Control | Management of Information
Condition No. | FERC Conditions | Primary Responsibility | Secondary Responsibility | Technip Condition Compliance Responsibilities | Owner Condition Compliance Responsibilities | Vendor / Subcontractor Deliverables Required
1 | Commonwealth LNG (CWLNG) shall follow the construction procedures and mitigation measures described in its application and supplements (including responses to staff data requests) and as identified in the EIS, unless modified by the Order. CWLNG must: a. request any modification to these procedures, measures, or conditions in a filing with the Secretary; b. justify each modification relative to site-specific conditions; c. explain how that modification provides an equal or greater level of environmental protection than the original measure; and d. receive approval in writing from the Director of the Office of Energy Projects (OEP), or the Director’s designee, before using that modification. | Owner | Technip | Technip shall provide comments regarding modifications of procedures, measures or conditions, justify modifications described in application, supplements, data requests and EIS. | Owner to file Variance Requests for approval to FERC. | No | X |  |  | S
2 | The Director of OEP, or the Director’s designee, has delegated authority to address any requests for approvals or authorizations necessary to carry out the conditions of the Order, and take whatever steps are necessary to ensure the protection of life, health, property, and the environment during construction and operation of the Commonwealth LNG Project (Project). This authority shall allow: a. the modification of conditions of the Order; b. stop-work authority and authority to cease operation; and c. the imposition of any additional measures deemed necessary to ensure continued compliance with the intent of the conditions of the Order as well as the avoidance or mitigation of unforeseen adverse environmental impacts resulting from Project construction and operation. | Owner | Technip | Technip shall provide documentation and comply with FERC directives as necessary (with Owner guidance) if the Director of OEP utilizes their delegated authority as detailed in Condition. | Owner to file Compliance Statement with FERC in General Conditions Implementation Plan. | No | X |  |  | S
3 | Prior to any construction, CWLNG shale file an afformatobe statement with the Secretary, certified by senior company officials, that all company personnel, environmental inspectors (EI), and contractor personnel will be informed of the EI’s authority and have been or will be trained on the implementation of the environmental mitigation measures appropriate to their jobs before becoming involved with construction and restoration activities. | Owner | Technip | Technip shall ensure their personnel and contractors have been trained on the implementation of the environmental mitigation measures appropriate to their jobs before becoming involved with construction and restoration activities. | Owner to file affirmative statement with FERC in General Conditions Implementation Plan and ensure compliance with statement. | No | X |  |  | S
4 | The authorized facility locations shall be as shown in the EIS, as supplemented by filed plot plans, alignment sheets, and facility diagrams. As soon as they are available, and before the start of construction, Commonwealth shall file with the Secretary any revised detailed plans, diagrams, and alignment sheets at a scale not smaller than 1:6,000 with station positions for all facilities approved by the Order. All requests for modifications of environmental conditions of the Order or site-specific clearances must be written and must specify locations designated on these plans, diagrams, and alignment sheets. | Owner | Technip | Technip shall provide revised detailed plans, diagrams and alignment sheets for revisions to the authorized facility locations shown in the EIS. | Owner to file revised detailed plans, diagrams, and alignments sheets for approval to FERC. | No | X | [16 empty] | S
5 | Commonwealth shall file with the Secretary detailed alignment maps/sheets and aerial photographs at a scale not smaller than 1:6,000 identifying all route realignments or facility relocations, staging areas, pipe storage yards, new access roads, and other areas that would be used or disturbed that have not been previously identified in filings with the Secretary. Approval for each of these areas must be explicitly requested in writing. For each area, the request must include a description of the existing land use or cover type, documentation of landowner approval, whether any cultural resources or federally listed threatened or endangered species would be affected, and whether any other environmentally sensitive areas are within or abutting the area. All areas shall be clearly identified on the maps, or aerial photographs. Use of each area must be approved in writing by the Director of OEP, or the Director’s designee, before construction in or near that area. This requirement does not apply to extra workspace allowed by the Commission’s Upland Erosion Control, Revegetation, and Maintenance Plan and/or minor field realignments per landowner needs and requirements which do not affect other landowners or sensitive environmental areas such as wetlands. Examples of alterations requiring approval include all route alignments and facility location changes resulting from: a. implementation of cultural resources mitigation measures; b. implementation of endangered, threatened, or special concern mitigation measures; c. recommendations by state regulatory authorities; and d. agreements with individual landowners that affect other landowners or could affect sensitive environmental areas. | Owner | Technip | Technip shall provide alignment maps/sheets and aerial photographs for route alignments, facility relocations, staging areas, pipe storage yards, new access roads and other areas that would be used or disturbed and have not been previously identified in filings. | Owner to file with FERC in General Condition Implementation Plan any revisions to the route or facility relocations, staging areas, pipe storage yards, new access roads or other areas not previously identified in filings for approval to FERC. | No | X | [16 empty] | S
6 | Within 60 days before construction begins, CWLNG shall each file Implementation Plans with the Secretary for review and written approval by the Director of OEP, or the Directors designee. CWLNG must file revisions to their plans as schedules change. The plans shall identify: a. how Commonwealth will implement the construction procedures and mitigation measures described in its application and supplements (including responses to staff data requests), identified in the EIS, and required by the Order; b. how Commonwealth will incorporate these requirements into the contract bid documents, construction contracts (especially penalty clauses and specifications), and construction drawings so that the mitigation required at each site is clear to onsite construction and inspection personnel; c. the number of EIs assigned, and how the company will ensure that sufficient personnel are available to implement the environmental mitigation; d. company personnel, including EIs and contractors, who will receive copies of the appropriate material; e. the location and dates of the environmental compliance training and instructions Commonwealth will give to all personnel involved with construction and restoration (initial and refresher training as the Project progresses and personnel change), with the opportunity for OEP staff to participate in the training session(s); f. the company personnel (if known) and specific portion of Commonwealth’s organization having responsibility for compliance; g. the procedures (including use of contract penalties) Commonwealth will follow if noncompliance occurs; and i. for each discrete facility, a Gantt or PERT chart (or similar project scheduling diagram), and dates for: ii, the completion of all required surveys and reports; iii. the environmental compliance training of onsite personnel; iv. the start of construction; and v. the start and completion of restoration. | Owner | Technip | Technip shall provide updates to schedule, how construction procedures will be implemented, Organizational chart for environmental responsibility to provide copies of environmental documents, environmental training records available on an as needed basis. Requirements in the contract bid, construction contracts and construction drawings so that mitigation at site is clear to onsite construction and inspection personnel. | Owner to file in the General Condition Implementation Plan construction procedures, mitigation measures, identify how Els assigned and sufficient personnel to implement mitigation, compliance training, organizational compliance responsibility, and contract penalties if noncompliance occurs. | No | X
7 | Commonwealth shall employ at least one EI for the Project. The EI(s) shall be: a. responsible for monitoring and ensuring compliance with all mitigation measures required by the Order and other grants, permits, certificates, or other authorizing documents; b. responsible for evaluating the construction contractor’s implementation of the environmental mitigation measures required in the contract (see condition 6 above) and any other authorizing document; c. empowered to order correction of acts that violate the environmental conditions of the Order, and any other authorizing document; d. a full-time position, separate from all other activity inspectors; e. responsible for documenting compliance with the environmental conditions of the Order, as well as any environmental conditions/permit requirements imposed by other federal, state, or local agencies; and f. responsible for maintaining status reports. | Owner | Technip | Technip acknowledges that the El(s) is responsible for evaluating the construction contractor’s implementation of the environmental mitigation measures required in the contract and is empowered to order correction of acts that violate the environmental conditions of the Order and any other authorizing document. Will provide environmental status updates to Owner on a weekly basis. | Owner to file Compliance Statement and responsible for status reports with FERC in General Conditions Implementation Plan. | No | X |  |  | S | S
8 | Beginning with the filing of its Implementation Plan, Commonwealth shall file updated status reports with the Secretary on a monthly basis until all construction and restoration activities are complete. Problems of a significant magnitude shall be reported to the FERC within 24 hours. On request, these status reports will also be provided to other federal and state agencies with permitting responsibilities. Status reports shall include: a. an update on Commonwealth’s efforts to obtain the necessary federal authorizations; b. project schedule, including current construction status of the project and work planned for the following reporting period; c. listing of all problems encountered, contractor nonconformance/deficiency logs, and each instance of noncompliance observed by the EI during the reporting period (both for the conditions imposed by the Commission and any environmental conditions/permit requirements imposed by other federal, state, or local agencies); d. a description of the corrective and remedial actions implemented in response to all instances of noncompliance, nonconformance, or deficiency; e the effectiveness of all corrective and remedial actions implemented; f. a description of any landowner/resident complaints which may relate to compliance with the requirements of the order, and the measures taken to satisfy their concerns; and g. copies of any correspondence received by Commonwealth from other federal, state, or local permitting agencies concerning instances of noncompliance, and Commonwealth’s response. | Owner | Technip | Technip shall provide status report that includes construction status and work planned, noncompliance and actions taken to remedy. | Owner to file Compliance Statement with FERC in General Conditions Implementation Plan and will file updated status reports that includes noncompliance, remedies, and resolution, effectiveness of actions and landowner issues with agency correspondence received and file on a monthly basis or within 24 hours for problems of a significant magnitude. | No | X |  |  |  | S
9 | CWLNG shall develop and implement an environmental complaint resolution procedure, and file such procedure with the Secretary, for review and approval by the Director of OEP, or the Director’s designee. The procedure shall provide landowners with clear and simple directions for identifying and resolving their environmental mitigation problems/concerns during construction of the project and restoration of the right-of-way. Prior to construction, Commonwealth shall mail the complaint procedures to each landowner whose property will be crossed by the project. a. In its letter to affected landowners, Commonwealth shall: i. provide a local contact that the landowners should call first with their concerns; the letter should indicate how soon a landowner should expect a response; ii. instruct the landowners that if they are not satisfied with the response, they should call Commonwealth's Hotline; the letter should indicate how soon to expect a response; and iii. instruct the landowners that if they are still not satisfied with the response from Commonwealth's Hotline, they should contact the Commission’s Landowner Helpline at 877-337-2237 or at LandownerHelp@ferc.gov. b. In addition, Commonwealth shall include in its monthly status report a copy of a table that contains the following information for each problem/concern: i. the identity of the caller and date of the call; i. the location by milepost and identification number from the authorized alignment sheet(s) of the affected property; ii. a description of the problem/concern; and iii. an explanation of how and when the problem was resolved, will be resolved, or why it has not been resolved. | Owner | NA | None | Owner to develop the compliant resolution procedure with FERC prior to construction. Owner will also mail the procedures to each landowner whose property that will be crossed by project and implement compliant procedures prior to construction. | No | X
10 | All conditions attached to the water quality certification issued by Louisiana Department of Environmental Quality constitute mandatory conditions of this Authorization Order. Prior to construction, Commonwealth shall file, for review and written approval of the Director of OEP, or the Director’s designee, any revisions to its project design necessary to comply with the water quality certification conditions. | Owner | Technip | Technip shall provide supporting documents to Owner for any revisions to the project design necessary to comply with the LDEQ water quality certification conditions. | Owner to file WQC and as relevant project design revisions as required. | No | X | [6 empty] | S |  |  |  | S
11 | Commonwealth must receive written authorization from the Director of OEP, or the Director’s designee, before commencing construction of any Project facilities. To obtain such authorization, Commonwealth must file with the Secretary documentation that it has received all applicable authorizations required under federal law (or evidence of waiver thereof). | Owner | NA | None | Owner to file Compliance Statement and updated Permits Table with FERC in General Conditions Implementation Plan. | No | X
12 | CWLNG must receive written authorization from the Director of OEP prior to introducing hazardous fluids into the liquefaction facilities. Instrumentation and controls, hazard detection, hazard control, and security components/systems necessary for the safe introduction of such fluids shall be installed and functional. | Owner | Technip | Technip shall provide supporting documentation as required and ensure that instrumentation and controls, hazard detection, hazard control, and security components/systems necessary for the safe introduction of such fluids shall be installed and functional. | Owner to file Compliance Statement with FERC in General Conditions Implementation Plan and will file request to introduce hazardous fluids into the LNG Facility when appropriate. | No | X |  | X |  |  |  | S (TBC) |  |  | S | [12 empty] | S | S
13 | Commonwealth must receive written authorization from the Director of OEP, or the Director’s designee, before placing into service the Project facilities. Such authorization will only be granted following a determination that the facilities have been constructed in accordance with FERC approval, can be expected to operate safely as designed, and the rehabilitation and restoration of areas affected by the project are proceeding satisfactorily. | Owner | Technip | Technip shall ensure that the Project facilities are constructed in accordance with FERC approval and to operate safely as designed. Technip to provide status of site rehabilitation and restoration. | Owner to file Compliance Statement with FERC in General Conditions Implementation Plan and will file request to place Project facilities into service when appropriate. | No | X
14 | Within 30 days of placing the authorized facilities in service, Commonwealth shall file an affirmative statement with the Secretary, certified by a senior company official: a. that the facilities have been constructed in compliance with all applicable conditions, and that continuing activities will be consistent with all applicable conditions; or b. identifying which of the conditions in the Order Commonwealth has complied with or will comply with. This statement shall also identify any areas affected by the project where compliance measures were not properly implemented, if not previously identified in filed status reports, and the reason for noncompliance. | Owner | Technip | Technip shall support Owner as necessary if there are any conditions not yet satisfied, or compliance measures not properly implemented at the time the authorized facilities are place in service. | Owner to file Compliance Statement with FERC in General Conditions Implementation Plan and will file affirmative statement certified by senior company official within 30 days of placing the authorized facilities into service. | No | X
15 | Prior to construction of the Project Pipeline, Commonwealth shall file with the Secretary for review and written approval by the Director of OEP, or the Director’s designee, an alternative contingency plan for crossing Highway 27/82 in the event that Commonwealth is unable to successfully complete the proposed horizontal directional drill of Highway 27/82. Commonwealth shall develop the contingency plan in consultation with the Louisiana Department of Transportation and Development. | Owner | NA | None | Owner has sole responsibility for Project Pipeline and will file compliance with FERC prior to construction of the Project Pipeline if contingency plan is required. | No | X
16 | Commonwealth shall successfully complete the Highway 27/82 crossing prior to the start of construction of the remainder of the Project Pipeline. | Owner | NA | None | Owner has sole responsibility for Project Pipeline and will reference condition prior to the start of construction of the remainder of the Project Pipeline. | No | X
17 | Prior to construction of the Project, Commonwealth shall file with the Secretary a copy of the determination of consistency with the Coastal Zone Management Program issued by the Louisiana Department of Natural Resources. | Owner | Technip | Technip shall support Owner as necessary, if changes occur to impact CZM. | Owner to file Compliance Statement and determination of consistency with FERC in General Conditions Implementation Plan. | No | X
18 | During construction activities at the Terminal, Commonwealth shall monitor noise levels between 7:00 p.m. and 7:00 a.m., document the noise levels in the construction status reports, and restrict the noise attributable to construction activities to no more than 55 A-weighted decibel (dBA) day-night sound level (Ldn) (48.6 dBA total noise impacts) at noise sensitive areas (NSA) 1 and 2. | Technip | Owner | Technip shall monitor noise levels between 7:00 p.m. and 7:00 a.m. during construction activities at the Terminal and restrict noise levels attributable to construction activities as proscribed in Condition. Technip to provide levels to Owner who will include in construction status reports. | Owner to document in construction status reports file with FERC. | Yes |  |  |  | X | X
19 | Commonwealth shall file a full power load noise survey with the Secretary for the Terminal no later than 60 days after each liquefaction train is placed into service. If the noise attributable to operation of the equipment at the Terminal exceeds an Ldn of 55 dBA at NSAs, within 60 days Commonwealth shall modify operation of the liquefaction facilities or install additional noise controls until a noise level below an Ldn of 55 dBA at the NSAs is achieved. Commonwealth shall confirm compliance with the above requirement by filing a second noise survey with the Secretary no later than 60 days after it installs the additional noise controls. | Owner | Technip | Technip shall provide Owner with noise survey data for each liquefaction train and make modifications or install additional noise controls as necessary if noise levels exceed authorized levels. | Owner to file Compliance Statement with FERC in General Conditions Implementation Plan and will file noise surveys with FERC after each liquefaction train is placed into service. | Yes | X | [9 empty] | X
20 | Commonwealth shall file a noise survey with the Secretary no later than 60 days after placing the entire Terminal into service. If a full load condition noise survey is not possible, Commonwealth shall provide an interim survey at the maximum possible horsepower load within 60 days of placing the Terminal into service and provide the full load survey within 6 months. If the noise attributable to operation of the equipment at the Terminal exceeds an Ldn of 55 dBA at any nearby NSA under interim or full horsepower load conditions, Commonwealth shall file a report on what changes are needed and shall install the additional noise controls to meet the level within 1 year of the in-service date. Commonwealth shall confirm compliance with the above requirement by filing an additional noise survey with the Secretary no later than 60 days after it installs the additional noise controls. | Owner | Technip | Technip shall provide Owner with noise survey data for entire Terminal and make modifications or install additional noise controls as necessary if noise levels exceed authorized levels. | Owner to file Compliance Statement with FERC in General Conditions Implementation Plan. Owner will file noise surveys with FERC no later than 60 days after placing the entire Terminal into service, operation less than 55 dBA at the NSA. | Yes | X | [9 empty] | X
21 | Prior to initial site preparation, Commonwealth shall file with the Secretary the following information, stamped and sealed by the professional engineer-of-record, registered in the State of Louisiana: a. finalized ground improvement solution of wick drains combined with surcharge for the Project site; b. site soil compaction via surcharge procedures and specifications; and c. finalized wick drains installation design package. | Technip | Owner | Technip shall provide PE stamped and sealed information for items a, b, and c. | Owner will review, format as necessary and file with FERC in Site Preparation Implementation Plan. | Yes |  | X |  |  |  | X | [6 empty] | X | X
22 | Prior to initial site preparation, Commonwealth shall file with the Secretary the following information, stamped and sealed by the professional engineer-of-record, registered in the State of Louisiana: a. the corrosion control and prevention plan for any underground piping, structures, foundations, equipment, and components; and b. the erosion control and prevention plan for the marine facility area. | Technip | Owner | Technip shall provide PE stamped and sealed information for items a and b. | Owner will review, format as necessary and file with FERC in Site Preparation Implementation Plan. | Yes |  | X |  |  |  | X | [8 empty] | X | [5 empty] | X (CP) | X |  |  | X | X | X | [5 empty] | X
23 | Prior to initial site preparation, Commonwealth shall file with the Secretary the finalized plot plan with final design of finished slopes and elevations contour lines for the Project site. The finalized plot plan shall be stamped and sealed by the professional engineer-of-record, registered in the State of Louisiana. | Technip | Owner | Technip shall provide PE stamped and sealed finalized plot with final design of finished slopes and elevation contours for the Project site. | Owner will review, format as necessary and file with FERC in Site Preparation Implementation Plan. | Yes |  | X | [10 empty] | X | X
24 | Prior to initial site preparation, Commonwealth shall file with the Secretary the finalized pile load test program (e.g., pile load test procedure, locations, configuration, quality assurance, and quality control, etc.). The filing shall be stamped and sealed by the professional engineer-of-record, registered in the State of Louisiana. | Technip | Owner | Technip shall provide PE stamped and sealed finalized pile load test program. | Owner will review, and file with FERC in Site Preparation Implementation Plan. | Yes |  | X |  | X |  | X | [6 empty] | X | S
25 | Prior to site initial preparation, Commonwealth shall file with the Secretary the final design of floodwalls (storm surge protection barriers) to comply with applicable code/standards requirements including but are not limited to National Fire Protection Association (NFPA) 59A (2019 edition) as incorporated by 33 Code of Federal Regulations (CFR) 127, and NFPA 59A (2001 edition) in 49 CFR 193. In addition, the floodwalls shall be designed and maintained in accordance with American Society of Civil Engineers (ASCE)/Structural Engineering Institute (SEI) 7 (2022 edition) or equivalent and ASCE/SEI 24 (2014 edition) or equivalent and to withstand a minimum of a 500-year mean occurrence interval in consideration of relative sea level rise, local subsidence, site settlement, shoreline recession, erosion and scour effect, and wind-driven wave effects, etc. The sea level rise and vertical land movement should be in accordance with at a minimum intermediate curve corresponding to design life of facility in Global and Regional Sea Level Rise Scenarios for the United States. U.S. Department of Commerce. National Ocean and Atmospheric Administration, National Ocean Service Center for Operational Oceanographic Products and Services, February 2022 or equivalent. The final design of floodwalls shall be stamped and sealed by the professional engineer-of-record, registered in the State of Louisiana. | Technip | Owner | Technip shall provide PE stamped and sealed final design of floodwalls (storm surge protection barriers). Technip will also be designed and maintain the floodwalls (per the applicable codes) per the terms of the EPC Agreement. In accordance with intermediate curve in Global and Regional Sea Level Rise Scenarios for the US. | Owner will review, format as necessary and file with FERC in Site Preparation Implementation Plan. Floodwall design may be filed in Site Preparation supplemental filing if final design is not completed at the time of the Site Preparation filing but only if approach is approved by FERC. | Yes |  | X |  |  |  | X | [6 empty] | S | X
26 | Prior to construction of final design, Commonwealth shall file with the Secretary consultation with U.S. Department of Transportation’s (DOT) Pipeline and Hazardous Materials Safety Administration (PHMSA) that determines whether the use of normally closed valves to remove stormwater from curbed areas will meet PHMSA regulations. | Owner | Technip | Technip shall provide documentation and support as necessary to support Owner consultation with DOT PHMSA. Stormwater removal system must comply with PHMSA regulations. | Owner will consult with DOT PHMSA and will file consultation with FERC prior to construction of final design of curbed areas. | No | X | [6 empty] | S
27 | Prior to construction of final design, Commonwealth shall file with the Secretary the following information, stamped and sealed by the professional engineer-of-record, registered in the State of Louisiana: a. the finalized settlement monitoring program and procedures for the Project site; b. the total and differential settlement of final designed structures, systems, and components foundations for the Project site; and c. the total and differential settlement monitoring system of LNG storage tank foundation design shall comply with applicable LNG industrial codes/standards, including but not limited to American Petroleum Institute (API) 620 (12th edition), API 625 (1st edition), API 650 (13th edition), API 653 (5th edition), and ACI 376 (2011 edition) or approved equivalents. | Technip | Owner | Technip shall provide PE stamped and sealed information for items a, b, and c. | Owner will review, format as necessary and file with FERC in the appropriate Final Design Implementation Plans. | Yes |  | X | [10 empty] | X | X | [17 empty] | X
28 | Prior to construction of final design, Commonwealth shall file with the Secretary the following information, stamped and sealed by the professional engineer-of-record, registered in the State of Louisiana: a. site preparation drawings and specifications; b. finalized civil design basis, criteria, specifications; c. LNG terminal structures, LNG storage tank, and foundation design drawings and calculations (including prefabricated and field constructed structures); d. seismic specifications for procured Seismic Category I equipment prior to the issuing of request for quotations; e. quality control procedures to be used for civil/structural design and construction; and f. a determination of whether soil improvement is necessary to counteract soil liquefaction. In addition, Commonwealth shall file, in its Implementation Plan, the schedule for producing this information. | Technip | Owner | Technip shall provide PE stamped and sealed information for items a- f. Technip will provide a schedule for producing the deliverables identified in a-f. | Owner will review, format as necessary and file with FERC in the appropriate implementation Plans. Items a, b, e, and f to be scheduled for producing will be filed with Site Preparation Implementation Plan. Items c and d to be filed in appropriate Final Design Implementation Plans. | Yes |  | X |  | X |  | X | [6 empty] | X | X |  |  | X |  |  | S |  |  |  |  | X |  | X (TBC) |  |  |  |  | X |  |  | X
29 | Prior to construction of the final design, Commonwealth shall file with the Secretary the finalized seismic monitoring program for the Project site. The seismic monitoring program shall comply with NFPA 59A (2019 edition) sections 8.4.14.10, 8.4.14.12, 8.4.14.12.1, 8.4.14.12.2, and 8.4.14.13; ACI 376 (2011 edition) sections 10.7.5 and 10.8.4; U.S. Nuclear Regulatory Commission Regulatory Guide (RG) 1.12 (Revision 3) sections 1 and 3 through 9 and all subsections, or equivalents subject to review and approval. A free-field seismic monitoring device should be included in the seismic monitoring program for the Project site. The proposed seismic monitoring system must include Installation location plot plan; description of the triaxial strong motion recorders or other seismic instrumentation; the proposed alarm set points and operating procedures (including emergency operating procedures) for control room operators in response to such alarms/data obtained from seismic instrumentation; and testing and maintenance procedures. | Technip | Owner | Technip shall provide finalized seismic monitoring program for the Project site. | Owner will review, format as necessary and file with FERC in the appropriate Final Design Implementation Plan. | Yes | [12 empty] | X | X | [8 empty] | X | [8 empty] | X
30 | Prior to construction of final design, Commonwealth shall file with the Secretary the settlement monitoring and maintenance plan that have been reviewed, approved, stamped and sealed by a professional engineer of record registered in the state of Louisiana, which ensures the facilities are protected for the life of the LNG terminal considering settlement, subsidence, and sea level rise. | Technip | Owner | Technip shall provide PE stamped and sealed final design elevation for the structures/buildings outside floodwalls area. | Owner will review, format as necessary and file with FERC in the appropriate Final Design Implementation Plan. | Yes |  | X | [10 empty] | X | [18 empty] | X
31 | Prior to construction of final design, Commonwealth shall file with the Secretary the final design elevation for the structures/buildings outside floodwalls area, including but are not limited to admin office/main control room, maintenance building, elevated flare, marine flare, jetty platform control room, etc. The final design elevation drawings and calculations shall be stamped and sealed by the professional engineer-of-record, registered in the State of Louisiana. | Technip | Owner | Technip shall provide PE stamped and sealed final design elevation for the structures/buildings outside floodwalls area. | Owner will review, format as necessary and file with FERC in the appropriate Final Design Implementation Plan. | Yes |  | X | [11 empty] | X | X |  | X | [7 empty] | X |  | X (TBC)
32 | Prior to initial site preparation, Commonwealth shall file an overall Project schedule, which includes the proposed stages of initial site preparation, construction, commissioning, and in-service plan relative to notice to proceed requests and related conditions. | Technip | Owner | Technip shall provide an overall Project schedule for inclusion in the Site Preparation IP. | Owner will review, format as necessary and file with FERC in Site Preparation Implementation Plan. | No | [34 empty] | X
33 | Prior to initial site preparation, CWLNG shall file procedures for controlling access during construction. | Technip | Owner | Technip shall provide procedures for access control during construction. | Owner will review, and file with FERC in the Site Implementation Plan. | Yes |  |  |  | X |  |  | X
34 | Prior to initial site preparation, Commonwealth shall file quality assurance and quality control procedures for construction activities, including transportation load monitoring for prefabricated process modules and LNG storage tanks. | Technip | Owner | Technip shall provide quality assurance and quality control procedures for construction activities. | Owner will review, format as necessary and file with FERC in Site Preparation Implementation Plan. | No |  |  |  | X (TBC) |  | X | [9 empty] | X | X |  |  | S | [9 empty] | X | X | X
35 | Prior to initial site preparation, Commonwealth shall file with the Secretary the finalized wind design basis for the project facility, which shall include the tornado loads determination and consideration of its load combination as required by ASCE/SEI 7 (2022 edition) or approved equivalent. | Technip | Owner | Technip shall provide finalized wind design basis for the project facility. | Owner will review, format as necessary and file with FERC in the Site Preparation Plan. | No | [13 empty] | X
36 | Prior to initial site preparation, Commonwealth shall file its design wind speed criteria for all other facilities not covered by PHMSA’s Letter of Determination to be designed to withstand wind speeds commensurate with the risk and reliability associated with the facilities in accordance with ASCE 7-22 or equivalent. | Technip | Owner | Technip shall provide design wind speed criteria for all facilities not covered by the PHMSA LOD. | Owner will review, format as necessary and file with FERC in the Site Preparation Implementation Plan. | No | [13 empty] | X
37 | Prior to initial site preparation, Commonwealth shall develop an Emergency Response Plan (ERP) (including evacuation and any sheltering and re-entry) and coordinate procedures with the U.S. Coast Guard (USCG); state, county, and local emergency planning groups; fire departments; state and local law enforcement; and other appropriate federal agencies. This plan shall be consistent with recommended and good engineering practices and based on potential impacts and onsets of hazards from accidental and intentional events along the LNG marine vessel route and potential impacts and onset of hazards from accidental and intentional events at the LNG terminal, including but not limited to a catastrophic failure of the largest LNG tank. This plan shall address any special considerations and pre-incident planning for infrastructure and public with access and functional needs and shall include at a minimum: a. materials and plans for periodic dissemination of public education and training materials for evacuation and/or shelter in place of the public within any transient hazard areas along the marine vessel route, and within LNG terminal hazard areas; b. plans to competently train emergency responders required to effectively and safely respond to hazardous material incidents including, but not limited to LNG fires and dispersion; c. plans to competently train emergency responders to effectively and safely evacuate or shelter public within transient hazard areas along the marine vessel route, and within hazard areas from LNG terminal; d. designated contacts with federal, state and local emergency response agencies responsible for emergency management and response within any transient hazard areas along the marine vessel route, and within hazard areas from LNG terminal; e. scalable procedures for the prompt notification of appropriate local officials and emergency response agencies based on the level and severity of potential incidents; f. scalable procedures for mobilizing response and establishing a unified command, including identification, location, and design of any emergency operations centers and emergency response equipment required to effectively and safely to respond to hazardous material incidents and evacuate or shelter public within transient hazard areas along the marine vessel route, and within LNG terminal hazard areas; g. scalable procedures for notifying public, including identification, location, design, and use of any permanent sirens or other warning devices required to effectively communicate and warn the public prior to onset of debilitating hazards within any transient hazard areas along the LNG marine vessel route and within hazard areas from LNG terminal; h. scalable procedures for evacuating the public, including identification, location, design, and use of evacuation routes/methods and any mustering locations required effectively and safely evacuate public within any transient hazard areas along the LNG marine transit route and within hazard areas from LNG terminal; and i. scalable procedures for sheltering the public, including identification, location, design, and use of any shelters demonstrated to be needed and demonstrated to effectively and safely shelter public prior to onset of debilitating hazards within transient hazard areas that may better benefit from sheltering in place (i.e., those within Zones of Concern 1 and 2), along the route of the LNG marine vessel and within hazard areas that may benefit from sheltering in place (i.e., those within areas of 1,600 British thermal units (BTU)/ft2 -hr and 10,000 BTU/ft2 -hr radiant heats from fires with farthest impacts, including from a catastrophic failure of largest LNG tank) of the LNG terminal. Commonwealth shall notify the FERC staff of all planning meetings in advance and shall report progress on the development of its ERP at 3‑month intervals. | Owner | Technip | Technip shall provide a finalized Construction, Commissioning and Start-up Emergency Response Plan. Technip will update and provide clarity on plans for emergency response, evacuation, how they will contact officials in an emergency response during construction, commissioning and start-up. | Owner will review and file Construction ERP with FERC in Site Preparation Implementation Plan. Owner will also file Draft version of Operations ERP in Site Preparation Implementation and will notify FERC of all planning meetings in advance and will report progress on the development of its ERP at 3-month intervals. | No | X |  | S | S | [5 empty] | S
38 | Prior to initial site preparation, Commonwealth shall file a Cost-Sharing Plan identifying the mechanisms for funding all Project-specific security/emergency management costs that would be imposed on state and local agencies. This comprehensive plan shall include funding mechanisms for the capital costs associated with any necessary security/emergency management equipment and personnel base. This plan shall include sustained funding of any requirement or resource gap analysis identified to effectively and safely evacuate and shelter public and to effectively and safely respond to hazardous material incidents consistent with recommended and good engineering practices. Commonwealth shall notify FERC staff of all planning meetings in advance and shall report progress on the development of its Cost Sharing Plan at 3-month intervals. | Owner | Technip | Technip shall provide clarity on plans for emergency response and security, hurricane preparedness and how they will contact officials in an emergency response during construction. | Owner to file Cost-Sharing Plan in Site Preparation Implementation Plan. | No | X
39 | Prior to construction of final design of any permanent facilities, Commonwealth shall file Emergency Response Plans and any associated Cost Sharing Plan provisions in coordination with federal, state, and local agencies for hazards that may reach State Highway 27, including identifying potential incidents, impact distances, and timing of the onset of hazards reaching State Highway 27, and measures to notify approaching highway traffic and evacuate persons from impacted areas as quickly as possible relative to the onset of hazards. The ERP and Cost Sharing Plans should discuss consideration of signage or equivalent, and maintenance thereof, to facilitate notification and evacuation. | Owner | NA | None | Owner to file with FERC Cost-Sharing Plan and Emergency Response Plans for hazards that may reach State Highway 27 during operations in the Site Implementation Plan. | No | X
40 | Prior to construction of final design, CWLNG shall file change logs that list and explain any changes made from the FEED provided in CWLNG’s application and filings. A list of all changes with an explanation for the design alteration shall be filed and all changes shall be clearly indicated on all diagrams and drawings. | Technip | Owner | Technip shall provide change logs with associated diagrams and drawings which clearly indicate changes from FEED to final design. | Owner to review format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | No | [33 empty] | X
41 | Prior to construction of final design, Commonwealth shall file information/revisions pertaining to Commonwealth’s response: numbers 15, 45, 65, and 106 of its February 4, 2020 filing; numbers 124, 125c, 127, 134, 135, 148, 153, 154, 155, 157, 161, 162, 164, 165, and 167 of its March 4, 2020 filing; numbers 7, 17, and 18 of its June 4, 2021 filing; numbers 5, 23, 27, 28, 29, 30, 31, 32, and 33 of its November 9, 2021 filing, which indicated features to be included or considered in the final design. | Technip | Owner | Technip shall provide information/revisions pertaining to all data request responses listed in the Condition. Information/revisions should be provided prior to the construction of final design for each of the various elements of the Project addressed in the data request responses. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). Owner will provide guidance on which responses should be included in the various IP filings for the separate work activities. | No | [8 empty] | X | X | [23 empty] | X
42 | Prior to construction of final design, Commonwealth shall file drawings and specifications for crash rated vehicle barriers in accordance with American Society for Testing and Materials (ASTM) F2656 (2015 edition) or approved equivalent at each facility entrance for access control. The crash rating vehicle type shall be supported by a security vulnerability assessment that takes into account the potential target attractiveness, threats, vulnerabilities, consequences, and mitigation effectiveness consistent with American Institute of Chemical Engineers, Guidelines for Analyzing and Managing the Security Vulnerabilities of Fixed Chemical Sites, 2003 or approved equivalent. The crash rating speed shall be supported by an analysis of the maximum attainable vehicle velocity based on vehicle type acceleration and road characteristics (e.g., straight length, radius of curvature, sloped/banked, coefficient of friction, etc.). | Technip | Owner | Technip shall provide drawings and specifications for crash rated vehicle barriers at each facility entrance for access control. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. | Yes | [6 empty] | X | [6 empty] | X
43 | Prior to construction of final design, Commonwealth shall file drawings of internal road vehicle protections, such as guard rails, barriers, and bollards to protect transfer piping, pumps, compressors, hydrants, monitors, etc. to ensure that they are located away from roadway or protected from inadvertent damage from vehicles. | Technip | Owner | Technip shall provide drawings of internal road vehicle protections. | Owner to review, format as necessary and file with FERC I appropriate Final Design Implementation Plan. | No | [9 empty] | S |  |  |  | X |  |  |  | X
44 | Prior to construction of final design, Commonwealth shall file drawings of the security fence. The fencing drawings shall provide details of fencing that demonstrates it is in accordance with NFPA 59A (2019 edition) or approved equivalent and would restrict and deter access around the entire facility and has a setback from exterior features (e.g., power lines, trees, etc.) and from interior features (e.g., piping, equipment, buildings, etc.) that does not allow the fence to be overcome. | Technip | Owner | Technip shall provide drawings of the security fence that are in accordance with NFPA 59A (2019 edition) or approved equivalent. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. | Yes | [13 empty] | X
45 | Prior to construction of final design, Commonwealth shall file security camera and intrusion detection drawings. The security camera drawings shall show the locations, mounting elevation, areas covered, and features of each camera (e.g., fixed, tilt/pan/zoom, motion detection alerts, low light, etc.) and shall provide camera coverage at access points and along the entire perimeter with redundancies and camera coverage interior of the facility to enable rapid monitoring of the terminal, including a camera at the top of each LNG storage tank, and coverage within pretreatment areas, within liquefaction areas, within truck transfer areas, within marine transfer areas, and within buildings. The drawings shall show or note the location and type of the intrusion detection and shall cover the entire perimeter of the facility. | Technip | Owner | Technip shall provide security camera and intrusion detection drawings. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. | Yes | [6 empty] | S | [16 empty] | X
46 | Prior to construction of final design, Commonwealth shall file photometric analyses or equivalent and associated lighting drawings. The lighting drawings shall show the location, elevation, type of light fixture, and lux levels of the lighting system and shall provide illumination along the perimeter of the terminal, process equipment, mooring points, and along paths/roads of access and egress to facilitate security monitoring and emergency response operations in accordance with API 540 (4th edition) or approved equivalent and applicable federal regulations. | Technip | Owner | Technip shall provide photometric analyses or equivalent and associated lighting drawings. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. | Yes | [6 empty] | S | [14 empty] | X
47 | Prior to construction of final design, Commonwealth shall file a plot plan of the final design showing all major equipment, structures, buildings, and impoundment systems. | Technip | Owner | Technip shall provide plot plan of the final design. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. | No | [8 empty] | S | [8 empty] | X
48 | Prior to construction of final design, Commonwealth shall file a building siting assessment to ensure plant buildings that are occupied or critical to the safety of the LNG plant are adequately protected from potential hazards involving fires and vapor cloud explosions. | Technip | Owner | Technip shall provide building site assessment. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. | No | [8 empty] | X | S |  |  |  |  | X | X
49 | Prior to construction of final design, Commonwealth shall file three-dimensional plant drawings to confirm plant layout for maintenance, access, egress, and congestion. | Technip | Owner | Technip shall provide three-dimensional plant drawings. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. | No | [9 empty] | X | [7 empty] | X
50 | Prior to construction of final design, Commonwealth shall file up-to-date process flow diagrams (PFDs), heat and mass balances (HMBs), and piping and instrument diagrams (P&IDs), including vendor P&IDs. The HMBs shall demonstrate a peak export rate of 9.5 million metric tones per annum. The P&IDs shall include the following information: a. equipment tag number, name, size, duty, capacity, and design conditions; b. equipment insulation type and thickness; c. storage tank pipe penetration size and nozzle schedule; d. valve high pressure side and internal and external vent locations; e. piping with line number, piping class specification, size, and insulation type and thickness; f. piping specification breaks and insulation limits; g. all control and manual valves numbered; h. relief valves with size and set points; and i. drawing revision number and date. | Technip | Owner | Technip shall provide PFDs, HMBs, and P&IDs with HMBs export rate of 9.5 mtpa. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. | Yes | [7 empty] | X | [10 empty] | X |  | S |  |  |  | X | X | X |  |  |  |  | X
51 | Prior to construction of final design, Commonwealth shall file P&IDs, specifications, and procedures that clearly show and specify the tie-in details required to safely connect subsequently constructed facilities with the operational facilities. | Technip | Owner | Technip shall provide P&IDs, specifications, and procedures that clearly show and specify the tie-in details. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. | No | [7 empty] | X | [9 empty] | X
52 | Prior to construction of final design, Commonwealth shall file a car seal and lock philosophy and car seal and lock program, including a list of all car-sealed and locked valves consistent with the P&IDs. The car seal and lock program should include monitoring and periodically reviewing correct car seal and lock placement and valve position. | Technip | Owner | Technip shall provide car seal and lock philosophy and car seal and lock program, including a list of all car-sealed and locked valves consistent with the P&IDs. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. | No | [7 empty] | X
53 | Prior to construction of final design, Commonwealth shall file information to demonstrate the Engineering Procurement and Construction (EPC) contractor has verified that all FEED hazard identification recommendations have been addressed. | Technip | Owner | Technip shall provide information and verification that all FEED hazard identification recommendations have been addressed. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. | No | [8 empty] | X
54 | Prior to construction of final design, Commonwealth shall file a hazard and operability review of the final design P&IDs, a list of the resulting recommendations, and action taken on the recommendations. The issued for construction P&IDs shall incorporate the hazard and operability review recommendations and justification shall be provided for any recommendations that are not implemented. | Technip | Owner | Technip shall provide hazard and operability review of the final design P&IDs, a list of the resulting recommendations, and action taken on the recommendations. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. | No | [8 empty] | X
55 | Prior to construction of final design, Commonwealth shall file design pressure and set point information for the piping, equipment, and pressure relief valves located between the inlet feed gas high integrity pressure protection system (HIPPS) and the downstream pressure regulators to demonstrate pressures would not exceed the design pressures of these components. | Technip | Owner | Technip shall provide design pressure and set point information for the piping, equipment, and pressure relief valves located between the inlet feed gas high integrity pressure protection system (HIPPS) and the downstream pressure regulators to demonstrate pressures would not exceed the design pressures of these components. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. | No | [7 empty] | X
56 | Prior to construction of final design, Commonwealth shall provide a check valve upstream of the acid gas removal column to prevent backflow or provide a dynamic simulation that shows that upon plant shutdown, the swan neck would be sufficient for this purpose. | Technip | Owner | Technip shall provide a check valve upstream of the acid gas removal column to prevent backflow or provide a dynamic simulation that shows that upon plant shutdown, the swan neck would be sufficient for this purpose. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan a dynamic simulation if Technip does not provide check valve. | No | [7 empty] | X
57 | Prior to construction of final design, Commonwealth shall specify a second source of vacuum breaker gas (i.e., pad gas) for the LNG storage tanks independent of the liquefaction facility. | Technip | Owner | Technip shall specify in final design a second source of vacuum breaker gas (i.e., pad gas) for the LNG storage tanks independent of the liquefaction facility. | Owner to reference Condition in appropriate Final Design Implementation Plan and reference P&ID (or other document) in which compliance is demonstrated. | No | [7 empty] | X | [23 empty] | X
58 | Prior to construction of final design, Commonwealth shall include LNG tank fill flow measurement with high flow alarm. | Technip | Owner | Technip shall include in final design LNG tank fill flow measurement with high flow alarm. | Owner to reference Condition in appropriate Final Design Implementation Plan and reference P&IDs (or other document) in which compliance is demonstrated. | No | [7 empty] | X | [14 empty] | X | [8 empty] | X
59 | Prior to construction of final design, Commonwealth shall specify a discretionary vent valve on each LNG storage tank that is operable through the Distributed Control System (DCS). In addition, a car sealed open manual block valve shall be provided upstream of the discretionary vent valve. | Technip | Owner | Technip shall specify in final design a discretionary vent valve on each LNG storage tank that is operable through the Distributed Control System (DCS). In addition, a car sealed open manual block valve shall be provided upstream of the discretionary vent valve. | Owner to reference Condition in appropriate Final Design Implementation Plan and reference P&IDs (or other document) in which compliance is demonstrated. | Yes | [7 empty] | X | [14 empty] | X | [8 empty] | X
60 | Prior to construction of final design, Commonwealth shall file the safe operating limits (upper and lower), alarm and shutdown set points for all instrumentation (e.g., temperature, pressures, flows, and compositions). | Technip | Owner | Technip shall provide the safe operating limits (upper and lower), alarm and shutdown set points for all instrumentation (e.g., temperature, pressures, flows, and compositions). | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. | Yes | [7 empty] | X | [14 empty] | X | X | X | X | X | X | X
61 | Prior to construction of final design, CWLNG shall file cause-and-effect matrices for the process instrumentation, fire and gas detection system, and ESD system for review and approval. The cause-and-effect matrices shall include alarms and shutdown functions, details of the voting and shutdown logic, and set points. | Technip | Owner | Technip shall provide cause-and-effect matrices for the process instrumentation, fire and gas detection system, and emergency shutdown system. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. | Yes | [7 empty] | X | [14 empty] | X |  | X | X | X (TBC) | X | X
62 | Prior to construction of final design, Commonwealth shall specify that all emergency shutdown valves are to be equipped with open and closed position switches connected to the Distributed Control System (DCS)/ safety instrument system (SIS). | Technip | Owner | Technip shall specify in final design that all emergency shutdown valves are to be equipped with open and closed position switches connected to the Distributed Control System (DCS)/ safety instrument system (SIS). | Owner to reference Condition in appropriate Final Design Implementation Plan and reference documents in which compliance is demonstrated. | Yes | [7 empty] | X | [14 empty] | X |  | X | X | X
63 | Prior to construction of final design, Commonwealth shall demonstrate that all electrical, instrument, and control systems at the project, which activate emergency systems or are relied upon for isolation or shutdowns, will be designed to withstand a 20-minute fire exposure per UL 1709 (6th edition) or approved equivalent. | Technip | Owner | Technip shall demonstrate in final design that all electrical, instrument, and control systems at the project, which activate emergency systems or are relied upon for isolation or shutdowns, will be designed to withstand a 20-minute fire exposure per UL 1709 (6th edition) or approved equivalent. | Owner to reference Condition in appropriate Final Design Implementation Plan and reference documents in which compliance is demonstrated. | Yes | [9 empty] | S | [11 empty] | S | X | X | X | X | X
64 | Prior to construction of final design, Commonwealth shall file an up-to-date equipment list, process and mechanical data sheets, and specifications. The specifications shall include: a. building specifications (e.g., control buildings, electrical buildings, compressor buildings, storage buildings, pressurized buildings, ventilated buildings, blast resistant buildings); b. mechanical specifications (e.g., piping, valve, insulation, rotating equipment, heat exchanger, storage tank and vessel, other specialized equipment); c. electrical and instrumentation specifications (e.g., power system, control system, SIS, cable, other electrical and instrumentation); and d. security and fire safety specifications (e.g., security, passive protection, hazard detection, hazard control, firewater). | Technip | Owner | Technip shall provide an up-to-date equipment list, process and mechanical data sheets, and specifications. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes |  |  |  | X (TBC) |  |  | S | X |  | X |  |  |  |  | X | X | X |  |  |  | X (TBC) | X | X (TBC) | X | X | X | X | X (TBC) | X (TBC) |  |  | X
65 | Prior to construction of final design, Commonwealth shall file a list of all codes and standards and the final specification document number where they are referenced. | Technip | Owner | Technip shall provide a list of all codes and standards and the final specification document number where they are referenced. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | No | [33 empty] | X
66 | Prior to construction of final design, Commonwealth shall file a complete specifications and drawings of the proposed LNG tank design and installation. | Technip | Owner | Technip shall provide complete specifications and drawings of the proposed LNG tank design and installation. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes | [31 empty] | X
67 | Prior to construction of final design, Commonwealth shall file an evaluation of emergency shutdown valve closure times. The evaluation shall account for the time to detect an upset or hazardous condition, notify plant personnel, and close the emergency shutdown valve(s). | Technip | Owner | Technip shall provide an evaluation of emergency shutdown valve closure times. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes | [8 empty] | X | X | [12 empty] | S |  | X | X | X
68 | Prior to construction of final design, Commonwealth shall file an evaluation of dynamic pressure surge effects from valve opening and closure times and pump operations that demonstrate that the surge effects do not exceed the design pressures. | Technip | Owner | Technip shall provide an evaluation of dynamic pressure surge effects from valve opening and closure times and pump operations that demonstrate that the surge effects do not exceed the design pressures. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes | [7 empty] | X
69 | Prior to construction of final design, Commonwealth shall demonstrate that, for hazardous fluids, piping and piping nipples 2 inches or less in diameter are designed to withstand external loads, including vibrational loads in the vicinity of rotating equipment and operator live loads in areas accessible by operators. | Technip | Owner | Technip shall demonstrate that, for hazardous fluids, piping and piping nipples 2 inches or less in diameter are designed to withstand external loads, including vibrational loads in the vicinity of rotating equipment and operator live loads in areas accessible by operators. | Owner to reference Condition in appropriate Final Design Implementation Plan and reference documents in which compliance is demonstrated. | Yes | [17 empty] | X | [6 empty] | X | X | X (TBC)
70 | Prior to construction of final design, Commonwealth shall clearly specify the responsibilities of the LNG tank contractor and the EPC contractor for the piping associated with the LNG storage tank. | Technip | Owner | Technip shall clearly specify the responsibilities of the LNG tank contractor and the EPC contractor for the piping associated with the LNG storage tank. | Owner to reference Condition in appropriate Final Design Implementation Plan and reference documents in which compliance is demonstrated. | No | [7 empty] | X | [23 empty] | X
71 | Prior to construction of final design, Commonwealth shall file the sizing basis and capacity for the final design of the flares and/or vent stacks as well as the pressure and vacuum relief valves for major process equipment, vessels, and storage tanks. | Technip | Owner | Technip shall provide the sizing basis and capacity for the final design of the flares and/or vent stacks as well as the pressure and vacuum relief valves for major process equipment, vessels, and storage tanks. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes | [7 empty] | X |  |  |  | X | [12 empty] | X | X | X |  |  |  |  | X
72 | Prior to construction of final design, Commonwealth shall file the sizing calculations for the PSVs of the following vessels: E-A0101 Inlet Gas Preheater, EA0403 Demethanizer Reboiler, E-A0301 Regeneration gas hot oil heater. Specifically, the calculations shall show the influence of the backpressure on these PSVs since they vent to the hot oil expansion drum (V-2101A) instead of the flare. | Technip | Owner | Technip shall provide the sizing calculations for the PSVs of the following vessels: E-A0101 Inlet Gas Preheater, E-A0403 Demethanizer Reboiler, E-A0301 Regeneration gas hot oil heater. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes | [7 empty] | X | [14 empty] | S
73 | Prior to construction of final design, Commonwealth shall specify the process vessels, and storage vessels for ethylene, propane, isopentane, condensate, hot oil, and LNG are installed with spare pressure relief valves to ensure overpressure protection during relief valve testing or maintenance. | Technip | Owner | Technip shall specify in final design the process vessels, and storage vessels for ethylene, propane, isopentane, condensate, hot oil, and LNG are installed with spare pressure relief valves to ensure overpressure protection during relief valve testing or maintenance. | Owner to reference Condition in appropriate Final Design Implementation Plan and reference documents in which compliance is demonstrated. | No | [7 empty] | X
74 | Prior to construction of final design, Commonwealth shall file an updated fire protection evaluation of the proposed facilities. A copy of the evaluation, a list of recommendations and supporting justifications, and actions taken on the recommendations shall be filed. The evaluation shall justify the type, quantity, and location of hazard detection and hazard control, passive fire protection, emergency shutdown and depressurizing systems, firewater, and emergency response equipment, training, and qualifications in accordance with NFPA 59A (2001). The justification for the flammable and combustible gas detection and flame and heat detection systems shall be in accordance with International Society of Automation (ISA) 84.00.07 (2018 edition) or approved equivalent methodologies and would need to demonstrate 90 % or more of releases (unignited and ignited) that could result in an off-site or cascading impact would be detected by two or more detectors and result in isolation and de inventory within 10 minutes. The analysis shall take into account the set points, voting logic, wind speeds, and wind directions. The justification for firewater shall provide calculations for all firewater demands based on design densities, surface area, and throw distance as well as specifications for the corresponding hydrant and monitors needed to reach and cool equipment. | Technip | Owner | Technip shall provide an updated fire protection evaluation of the proposed facilities. A copy of the evaluation, a list of recommendations and supporting justifications, and actions taken on the recommendations to be provided by Technip. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | No | [9 empty] | X
75 | Prior to construction of final design, Commonwealth shall file spill containment system drawings with dimensions and slopes of curbing, trenches, impoundments, tertiary containment and capacity calculations considering any foundations and equipment within impoundments, as well as the sizing and design of the downcomers. The spill containment drawings shall show containment for all hazardous fluids including all liquids handled above their flashpoint, from the largest flow from a single line for 10 minutes, including de-inventory, or the maximum liquid from the largest vessel (or total of impounded vessels) or otherwise demonstrate that providing spill containment would not significantly reduce the flammable vapor dispersion or radiant heat consequences of a spill. | Technip | Owner | Technip shall provide spill containment system drawings with dimensions and slopes of curbing, trenches, impoundments, tertiary containment and capacity calculations considering any foundations and equipment within impoundments, as well as the sizing and design of the down comers. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes | [8 empty] | X | S |  |  |  | X
76 | Prior to construction of final design, Commonwealth shall file an analysis that demonstrates the flammable vapor dispersion from design spills would be prevented from dispersing underneath the elevated LNG storage tanks, or the LNG storage tanks would be able to withstand an overpressure due to ignition of the flammable vapor that disperses underneath the elevated LNG storage tanks. | Technip | Owner | Technip shall provide an analysis that demonstrates the flammable vapor dispersion from design spills would be prevented from dispersing underneath the elevated LNG storage tanks, or the LNG storage tanks would be able to withstand an overpressure due to ignition of the flammable vapor that disperses underneath the elevated LNG storage tanks. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes | [8 empty] | S | [22 empty] | X
77 | Prior to construction of final design, Commonwealth shall file an analysis that demonstrates the flammable vapor dispersion from design spills would be prevented from dispersing underneath the elevated control room, or the control room would be able to withstand an overpressure due to ignition of the flammable vapor that disperses underneath the elevated control room. | Technip | Owner | Technip shall provide an analysis that demonstrates the flammable vapor dispersion from design spills would be prevented from dispersing underneath the elevated control room, or the control room would be able to withstand an overpressure due to ignition of the flammable vapor that disperses underneath the elevated control room. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes | [8 empty] | X | S
78 | Prior to construction of final design, Commonwealth shall file a technical review of its proposed facility design that evaluates other potential locations for the proposed control room, or additional mitigation measures to protection the control room from high radiant heats. | Technip | Owner | Technip shall provide a technical review of its proposed facility design that evaluates other potential locations for the proposed control room, or additional mitigation measures to protect the control room from high radiant heats. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes | [8 empty] | X | S
79 | Prior to construction of final design, Commonwealth shall file electrical area classification drawings, including cross sectional drawings. The drawings shall demonstrate compliance with NFPA 59A (2019 edition), NFPA 70 (2017 edition), NFPA 497 (2017 edition), and API RP 500 (3rd edition), or approved equivalents. In addition, the drawings shall include revisions to the electrical area classification design or provide technical justification that supports the electrical area classification of the following areas using most applicable API RP 500 figures (e.g., figures 20 and 21) or hazard modeling of various release rates from equivalent hole sizes and wind speeds (see NFPA 497 release rate of 1 lbmole/ minute). | Technip | Owner | Technip shall provide file electrical area classification drawings, including cross sectional drawings. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | No | [9 empty] | X | [11 empty] | X
80 | Prior to construction of final design, Commonwealth shall file analysis of the buildings containing hazardous fluids and the ventilation calculations that limit concentrations below the lower flammable limits (LFL) (e.g., 25-percent LFL), including an analysis of off gassing of hydrogen in battery rooms, and shall also provide hydrogen detectors that alarm (e.g., 20- to 25-percent LFL) and initiate mitigative actions (e.g., 40- to 50-percent LFL) in accordance with NFPA 59A (2019 edition) and NFPA 70 (2017 edition), or approved equivalents. | Technip | Owner | Technip shall provide analysis of the buildings containing hazardous fluids and the ventilation calculations. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes | [9 empty] | S | [11 empty] | X | X | X |  | X
81 | Prior to construction of final design, Commonwealth shall file drawings and details of how process seals or isolations installed at the interface between a flammable fluid system and an electrical conduit or wiring system meet the requirements of NFPA 59A (2001) or approved equivalent. | Technip | Owner | Technip shall provide drawings and details of how process seals or isolations installed at the interface between a flammable fluid system and an electrical conduit or wiring system meet the requirements of NFPA 59A (2001) or approved equivalent. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | [8 empty] | S | S | S | [11 empty] | X
82 | Prior to construction of final design, Commonwealth shall file details of an air gap or vent installed downstream of process seals or isolations installed at the interface between a flammable fluid system and an electrical conduit or wiring system. Each air gap shall vent to a safe location and be equipped with a leak detection device that shall continuously monitor for the presence of a flammable fluid, alarm the hazardous condition, and shut down the appropriate systems. | Technip | Owner | Technip shall provide details of an air gap or vent installed downstream of process seals or isolations installed at the interface between a flammable fluid system and an electrical conduit or wiring system. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | No | [9 empty] | X | [11 empty] | X | X | X
83 | Prior to construction of final design, Commonwealth shall file complete drawings and a list of the hazard detection equipment. The drawings shall clearly show the location and elevation of all detection equipment as well as their coverage area. The list shall include the instrument tag number, type and location, alarm indication locations, and shutdown functions of the hazard detection equipment. | Technip | Owner | Technip shall provide complete drawings and a list of the hazard detection equipment. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | [10 empty] | X | [12 empty] | X | X
84 | Prior to construction of final design, Commonwealth shall file a technical review of facility design that: a. identifies all combustion/ventilation air intake equipment and the distances to any possible flammable gas or toxic release; and b. demonstrates that these areas are adequately covered by hazard detection devices and indicates how these devices would isolate or shutdown any combustion or heating ventilation and air conditioning equipment whose continued operation could add to or sustain an emergency. | Technip | Owner | Technip shall provide a technical review of facility design pertaining to items a and b. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes | [9 empty] | X | [11 empty] | X | X (TBC) |  |  |  |  | X | X
85 | Prior to construction of final design, Commonwealth shall file a design that includes hazard detection suitable to detect high temperatures and smoldering combustion products in electrical buildings and control room buildings. | Technip | Owner | Technip shall provide a design that includes hazard detection suitable to detect high temperatures and smoldering combustion products in electrical buildings and control room buildings. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes | [9 empty] | X |  |  |  |  | X | X | [5 empty] | X | X | X
86 | Prior to construction of final design, Commonwealth shall file an evaluation of the voting logic and voting degradation for hazard detectors. | Technip | Owner | Technip shall provide an evaluation of the voting logic and voting degradation for hazard detectors. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes | [8 empty] | X | X | [14 empty] | X (TBC) | X (TBC) | X (TBC)
87 | Prior to construction of final design, Commonwealth shall file a list of alarm and shutdown set points for all hazard detectors that account for the calibration gas of the hazard detectors when determining the lower flammable limit set points for methane, ethylene, propane, isopentane, and condensate. | Technip | Owner | Technip shall provide a list of alarm and shutdown set points for all hazard detectors that account for the calibration gas of the hazard detectors when determining the lower flammable limit set points for methane, ethylene, propane, isopentane, and condensate. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes | [7 empty] | X |  | X | [12 empty] | X |  | X | X
88 | Prior to construction of final design, Commonwealth shall file a list of alarm and shutdown set points for all hazard detectors that account for the calibration gas of hazard detectors when determining the set points for toxic components such as condensate and hydrogen sulfide. | Technip | Owner | Technip shall provide a list of alarm and shutdown set points for all hazard detectors that account for the calibration gas of hazard detectors when determining the set points for toxic components such as condensate and hydrogen sulfide. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes | [7 empty] | X |  | X | [12 empty] | X |  | X (TBC) | X (TBC) | X (TBC)
89 | Prior to construction of final design, Commonwealth shall file a drawing showing the location of the emergency shutdown buttons, including, but not limited to the refrigerant storage, condensate storage, and LNG storage areas. Emergency shutdown buttons shall be easily accessible, conspicuously labeled, and located in an area which would be accessible during an emergency. | Technip | Owner | Technip shall provide a drawing showing the location of the emergency shutdown buttons. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes | [9 empty] | X | [12 empty] | X |  | X | X | [5 empty] | X
90 | Prior to construction of final design, Commonwealth shall file facility plan drawings and a list of the fixed and wheeled dry-chemical, hand-held fire extinguishers, and other hazard control equipment. Plan drawings shall clearly show the location by tag number of all fixed, wheeled, and hand-held extinguishers and shall demonstrate the spacing of extinguishers meet prescribed NFPA 10 (2018 edition) or approved equivalent travel distances. The list shall include the equipment tag number, type, capacity, equipment covered, discharge rate, and automatic and manual remote signals initiating discharge of the units and shall demonstrate they meet NFPA 59A (2019 edition) or approved equivalent. | Technip | Owner | Technip shall provide facility plan drawings and a list of the fixed and wheeled dry-chemical, hand-held fire extinguishers, and other hazard control equipment. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | No | [9 empty] | X
91 | Prior to construction of final design, Commonwealth shall file drawings and specifications for the structural passive protection systems to protect equipment and supports from cryogenic releases. | Technip | Owner | Technip shall provide drawings and specifications for the structural passive protection systems to protect equipment and supports from cryogenic releases. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes | [8 empty] | X | X | [6 empty] | X | [7 empty] | X | X | X
92 | Prior to construction of final design, Commonwealth shall file calculations or test results for the structural passive protection systems to protect equipment and supports from cryogenic releases. | Technip | Owner | Technip shall provide calculations or test results for the structural passive protection systems to protect equipment and supports from cryogenic releases. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes | [8 empty] | X | X | [14 empty] | X | X | X
93 | Prior to construction of final design, Commonwealth shall file drawings and specifications for the structural passive protection systems to protect equipment and supports from pool and jet fires. | Technip | Owner | Technip shall provide drawings and specifications for the structural passive protection systems to protect equipment and supports from pool and jet fires. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes | [8 empty] | X | X | [6 empty] | X | [7 empty] | X | X | X
94 | Prior to construction of final design, Commonwealth shall file a detailed quantitative analysis to demonstrate that adequate mitigation would be provided for each pressure vessel that could fail within the 4,000 BTU/ft2-hr zone from a pool or jet fires; each critical structural component (including the LNG marine vessel) and emergency equipment item that could fail within the 4,900 BTU/ft2-hr zone from a pool or jet fire; and each occupied building that could expose unprotected personnel within the 1,600 BTU/ft2-hr zone from a pool or jet fire. Trucks at truck transfer stations shall be included in the analysis of potential pressure vessel failures, as well as measures needed to prevent cascading impact due to the 10-minute sizing spill at the marine area. A combination of passive and active protection for pool fires and passive and/or active protection for jet fires shall be provided and demonstrate the effectiveness and reliability. Effectiveness of passive mitigation shall be supported by calculations or test results for the thickness limiting temperature rise over the fire duration, and active mitigation shall be supported by reliability information by calculations or test results, such as demonstrating flow rates and durations of any cooling water would mitigate the heat absorbed by the component. The total firewater demand shall account for all components that could fail to a pool or jet fire. | Technip | Owner | Technip shall provide a detailed quantitative analysis to demonstrate that adequate mitigation for each pressure vessel that could fail within the 4,000 BTU/ft2-hr zone from a pool or jet fires; each critical structural component (including the LNG marine vessel) and emergency equipment item that could fail within the 4,900 BTU/ft2- hr zone from a pool or jet fire; and each occupied building that could expose unprotected personnel within the 1,600 BTU/ft2-hr zone from a pool or jet fire. Trucks at truck transfer stations shall be included in the analysis of potential pressure vessel failures, as well as measures needed to prevent cascading impact due to the 10-minute sizing spill at the marine area. A combination of passive and active protection for pool fires and passive and/or active protection for jet fires shall be provided and demonstrate the effectiveness and reliability. Effectiveness of passive mitigation shall be supported by calculations or test results for the thickness limiting temperature rise over the fire duration, and active mitigation shall be supported by reliability information by calculations or test results, such as demonstrating flow rates and durations of any cooling water would mitigate the heat absorbed by the component. The total firewater demand shall account for all components that could fail to a pool or jet fire. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes | [8 empty] | X | X
95 | Prior to construction of final design, Commonwealth shall file an evaluation and associated specifications, drawings, and datasheets for transformers demonstrating how it would prevent cascading damage of transformers (e.g., fire walls or spacing) in accordance with NFPA 850 (2015 edition) or approved equivalent. | Technip | Owner | Technip shall provide an evaluation and associated specifications, drawings, and datasheets for transformers. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes | [21 empty] | X
96 | Prior to construction of final design, Commonwealth shall file facility plan drawings showing the proposed location of the firewater and any foam systems. Plan drawings shall clearly show the location of firewater and foam piping, post indicator and sectional valves, and the location and area covered by, each monitor, hydrant, hose, water curtain, deluge system, foam system, water-mist system, and sprinkler. The drawings shall demonstrate that each process area, fire zone, or other sections of piping with several users can be isolated with post indicator or sectional valves and that firewater coverage is provided by at least two monitors or hydrants with sufficient firewater flow to cool exposed surfaces subjected to a fire. The drawings shall also include piping and instrumentation diagrams of the firewater and foam systems. | Technip | Owner | Technip shall provide facility plan drawings showing the proposed location of the firewater and any foam systems. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | No | [9 empty] | X
97 | Prior to construction of final design, Commonwealth shall specify that the firewater pump shelter is designed to remove the largest firewater pump or other component for maintenance with an overhead or external crane. | Technip | Owner | Technip shall specify in the final design that the firewater pump shelter is designed to remove the largest firewater pump or other component for maintenance with an overhead or external crane. | Owner to reference Condition in appropriate Final Design Implementation Plan and reference documents in which compliance is demonstrated. | Yes | [9 empty] | X | [14 empty] | X
98 | Prior to construction of final design, Commonwealth shall demonstrate that the fire water storage tank is in compliance with NFPA 22 (2018 edition) or approved equivalent. | Technip | Owner | Technip shall demonstrate that the firewater storage tank is in compliance with NFPA 22 (2018 edition) or approved equivalent. | Owner to reference Condition in appropriate Final Design Implementation Plan and reference documents in which compliance is demonstrated. | Yes | [9 empty] | X | [16 empty] | X
99 | Prior to construction of final design, Commonwealth shall specify that the fire water flow test meter is equipped with a transmitter and that a pressure transmitter is installed upstream of the flow transmitter. The flow transmitter and pressure transmitter shall be connected to the DCS and recorded. | Technip | Owner | Technip shall specify in the final design that the firewater flow test meter is equipped with a transmitter and that a pressure transmitter is installed upstream of the flow transmitter. The flow transmitter and pressure transmitter shall be connected to the DCS and recorded. | Owner to reference Condition in appropriate Final Design Implementation Plan and reference documents in which compliance is demonstrated. | No | [9 empty] | X | [12 empty] | X
100 | Prior to construction of final design, Commonwealth shall file drawings of the storage tank piping support structure and support of horizontal piping at grade including pump columns, relief valves, pipe penetrations, instrumentation, and appurtenances. | Technip | Owner | Technip shall provide drawings of the storage tank piping support structure and support of horizontal piping at grade including pump columns, relief valves, pipe penetrations, instrumentation, and appurtenances. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes | [13 empty] | X |  |  |  | X | [13 empty] | X
101 | Prior to construction of final design, Commonwealth shall file the structural analysis of the LNG storage tank and outer containment demonstrating they are designed to withstand all loads and combinations, including shipping loads. | Technip | Owner | Technip shall provide the structural analysis of the LNG storage tank and outer containment demonstrating they are designed to withstand all loads and combinations, including shipping loads. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes | [31 empty] | X
102 | Prior to construction of the final design, Commonwealth shall file the finalized projectile/missile impact analysis to demonstrate that the outer concrete container wall of the full containment LNG storage tank could withstand projectile/missile impact. The analysis shall detail the projectile/missile speeds and characteristics and methods used to determine penetration resistance and perforation depths. The finalized projectile/missile impact analysis shall be stamped and sealed by the professional engineer-of-record, registered in the State of Louisiana. | Technip | Owner | Technip shall provide the finalized PE stamped and sealed projectile/missile impact analysis. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes |  | X | [29 empty] | X
103 | Prior to construction of final design, Commonwealth shall file an analysis of the structural integrity of the outer containment of the full containment LNG storage tank demonstrating it can withstand the radiant heat from a roof tank top fire or adjacent tank roof fire. | Technip | Owner | Technip shall provide an analysis of the structural integrity of the outer containment of the full containment LNG storage tank demonstrating it can withstand the radiant heat from a roof tank top fire or adjacent tank roof fire. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes | [31 empty] | X
104 | Prior to construction of final design, Commonwealth shall file an analysis of the structural integrity of the outer containment of the full containment LNG storage tank demonstrating it can withstand the thermal shock caused by a failure of the inner tank. | Technip | Owner | Technip shall provide an analysis of the structural integrity of the outer containment of the full containment LNG storage tank demonstrating it can withstand the thermal shock caused by a failure of the inner tank. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Yes | [31 empty] | X
105 | Prior to commissioning, Commonwealth shall file a detailed schedule for commissioning through equipment startup. The schedule shall include milestones for all procedures and tests to be completed: prior to introduction of hazardous fluids and during commissioning and startup. Commonwealth shall file documentation certifying that each of these milestones has been completed before authorization to commence the next phase of commissioning and startup will be issued. | Technip | Owner | Technip shall provide a detailed schedule for commissioning through equipment startup. | Owner to review, format as necessary and file with FERC in appropriate Commissioning Implementation Plan(s). | No |  |  | X | [31 empty] | X
106 | Prior to commissioning, Commonwealth shall file detailed plans and procedures for: testing the integrity of onsite mechanical installation; functional tests; introduction of hazardous fluids; operational tests; and placing the equipment into service. | Technip | Owner | Technip shall provide detailed plans and procedures for: testing the integrity of onsite mechanical installation; functional tests; introduction of hazardous fluids; operational tests; and placing the equipment into service. | Owner to review, format as necessary and file with FERC in appropriate Commissioning Implementation Plan(s). | Yes |  |  | X
107 | Prior to commissioning, Commonwealth shall file settlement results from the hydrostatic tests of the LNG storage containers and shall file a plan to periodically verify settlement is as expected and does not exceed the applicable criteria set forth in API 620 (12th edition), API 625 (1st edition), API 650 (13th edition), API 653 (5th edition), and ACI 376 (2011 edition) or approved equivalents. The program shall also specify what actions would be taken after various levels of seismic events. | Technip | Owner | Technip shall provide settlement results from the hydrostatic tests of the LNG storage containers and a plan to periodically verify settlement. The program shall also specify what actions would be taken after various levels of seismic events. | Owner to review, format as necessary and file with FERC in appropriate Commissioning Implementation Plan(s). | Yes |  |  | X | [9 empty] | X | [18 empty] | X
108 | Prior to commissioning, Commonwealth shall file the operation and maintenance procedures and manuals, as well as safety procedures, hot work procedures and permits, abnormal operating conditions reporting procedures, simultaneous operations procedures, and management of change procedures and forms. | Technip | Owner | Technip shall provide operation and maintenance procedures and manuals, as well as safety procedures, hot work procedures and permits, abnormal operating conditions reporting procedures, simultaneous operations procedures, and management of change procedures and forms. | Owner to review, format as necessary and file with FERC in appropriate Commissioning Implementation Plan(s). | No |  |  | X |  | X
109 | Prior to commissioning, Commonwealth shall file a plan for clean-out, dry-out, purging, and tightness testing. This plan shall address the requirements of the American Gas Association’s Purging Principles and Practice and shall provide justification if not using an inert or non-flammable gas for clean-out, dry-out, purging, and tightness testing. | Technip | Owner | Technip shall provide a plan for clean-out, dry-out, purging, and tightness testing. | Owner to review, format as necessary and file with FERC in appropriate Commissioning Implementation Plan(s). | No |  |  | X
110 | Prior to commissioning, Commonwealth shall tag all equipment, instrumentation, and valves in the field, including drain valves, vent valves, main valves, and car sealed or locked valves. | Technip | Owner | Technip shall tag all equipment, instrumentation, and valves in the field, including drain valves, vent valves, main valves, and car sealed or locked valves. | Owner to reference Condition in appropriate Commissioning Implementation Plan and reference documents in which compliance is demonstrated. | Yes |  |  |  | X | [18 empty] | X |  | X | X | X | X | X |  |  | X
111 | Prior to commissioning, Commonwealth shall file a plan to maintain a detailed training log to demonstrate that operating, maintenance, and emergency response staff have completed the required training. | Owner | Technip | Owner to file with FERC a plan to maintain a detailed training log to demonstrate that CWLNG operating, maintenance, and emergency response staff have completed the required training. | Technip to ensure that training logs are maintained through construction, commissioning and start-up to demonstrate that operating, maintenance, and emergency response staff have completed the required training. Training logs should be made available for FERC review if requested. | No | X |  | S | S
112 | Prior to commissioning, Commonwealth shall file the procedures for pressure/leak tests which address the requirements of American Society of Mechanical Engineers (ASME) Boiler and Pressure Vessel Code Section VIII (2017 edition) and ASME B31.3 (2016 edition) or approved equivalents. In addition, Commonwealth shall file a line list of pneumatic and hydrostatic test pressures. | Technip | Owner | Technip shall provide the procedures for pressure/leak tests and a line list of pneumatic and hydrostatic test pressures. | Owner to review, format as necessary and file with FERC in appropriate Commissioning Implementation Plan(s). | Yes |  |  | X | X | [20 empty] | X | X | X
113 | Prior to introduction of hazardous fluids, Commonwealth shall complete and document a pre-startup safety review to ensure that installed equipment meets the design and operating intent of the facility. The pre-startup safety review shall include any changes since the last hazard review, operating procedures, and operator training. A copy of the review with a list of recommendations, and actions taken on each recommendation, shall be filed. | Technip | Owner | Technip shall complete and document a pre-startup safety review and provide a copy of the review with a list of recommendations and actions taken on each recommendation. | Owner to review, format as necessary and file with FERC in appropriate Hazardous Fluids Implementation Plan(s). | No |  |  | X | [6 empty] | S
114 | Prior to introduction of hazardous fluids, Commonwealth shall complete and document all pertinent tests (Factory Acceptance Tests, Site Acceptance Tests, Site Integration Tests) associated with the DCS and SIS that demonstrates full functionality and operability of the system. | Technip | Owner | Technip shall complete and document all pertinent tests (Factory Acceptance Tests, Site Acceptance Tests, Site Integration Tests) associated with the DCS and SIS that demonstrates full functionality and operability of the system. | Owner to reference Condition in appropriate Hazardous Fluids Implementation Plan. | Yes |  |  | X | [19 empty] | X |  | X | X
115 | Prior to introduction of hazardous fluids, Commonwealth shall develop, file, and implement an alarm management program consistent with ISA 18.2 (2016 edition) or approved equivalent to reduce alarm complacency and maximize the effectiveness of operator response to alarms. | Technip | Owner | Technip shall develop, provide and implement an alarm management program. | Owner to review, format as necessary and file with FERC in appropriate Hazardous Fluids Implementation Plan(s). | No | [22 empty] | X
116 | Prior to introduction of hazardous fluids, Commonwealth shall complete and document a clean agent acceptance tests. | Technip | Owner | Technip shall complete and document a clean agent acceptance tests. | Owner to reference Condition in appropriate Hazardous Fluids Implementation Plan. | No |  |  | X | [6 empty] | S
117 | Prior to introduction of hazardous fluids, Commonwealth shall complete and document a firewater pump acceptance test and firewater monitor and hydrant coverage test. The actual coverage area from each monitor and hydrant shall be shown on facility plot plan(s). | Technip | Owner | Technip shall complete and document a firewater pump acceptance test and firewater monitor and hydrant coverage test. The actual coverage area from each monitor and hydrant shall be shown on facility plot plan(s). | Owner to reference Condition in appropriate Hazardous Fluids Implementation Plan. | Yes |  |  | X | [6 empty] | X
118 | Prior to introduction of hazardous fluids, Commonwealth shall complete and document foam system and sprinkler system acceptance tests. | Technip | Owner | Technip shall complete and document foam system and sprinkler system acceptance tests. | Owner to reference Condition in appropriate Hazardous Fluids Implementation Plan. | Yes |  |  | X | [6 empty] | S | [14 empty] | X | X | X
119 | Commonwealth shall file a request for written authorization from the Director of OEP prior to unloading or loading the first LNG commissioning cargo. After production of first LNG, Commonwealth shall file weekly reports on the commissioning of the proposed systems that detail the progress toward demonstrating the facilities can safely and reliably operate at or near the design production rate. The reports shall include a summary of activities, problems encountered, and remedial actions taken. The weekly reports shall also include the latest commissioning schedule, including projected and actual LNG production by each liquefaction train, LNG storage inventories in each storage tank, and the number of anticipated and actual LNG commissioning cargoes, along with the associated volumes loaded or unloaded. Further, the weekly reports shall include a status and list of all planned and completed safety and reliability tests, work authorizations, and punch list items. Problems of significant magnitude shall be reported to the FERC within 24 hours. | Owner | Technip | Technip shall support Owner with information required for the weekly reports. | Owner to reference Condition and request written authorization from the Director of OEP prior to unloading or loading the first LNG commissioning cargo. After production of first LNG Owner will file weekly reports. Significant problems reported to FERC within 24 hours. | No | X | [5 empty] | S | [15 empty] | S | S
120 | Prior to commencement of service, Commonwealth shall file a request for written authorization from the Director of OEP. Such authorization would only be granted following a determination by the USCG, under its authorities under the Ports and Waterways Safety Act, the Magnuson Act, the Maritime Transportation Security Act of 2002, and the Security and Accountability For Every Port Act, that appropriate measures to ensure the safety and security of the facility and the waterway have been put into place by Commonwealth or other appropriate parties. | Owner | Technip | Technip shall support Owner to ensure appropriate safety and security measures have been put into place. | Owner to file request for written authorization to commence service. | No | X | [5 empty] | S | [15 empty] | S | S
121 | Prior to commencement of service, Commonwealth shall file any proposed revisions to the security plan and physical security of the plant. | Technip | Owner | Technip shall provide any proposed revisions to the security plan and physical security of the plant. | Owner to file any proposed revisions in Commencement of Service authorization request. | No |  |  |  | X |  |  | X
122 | Prior to commencement of service, Commonwealth shall label piping with fluid service and direction of flow in the field consistent with ASME A13.1 (2007 edition) or approved equivalent, in addition to the pipe labeling requirements of NFPA 59A (2001). | Technip | Owner | Technip shall label piping with fluid service and direction of flow in the field. | Owner to reference Condition in Commencement of Service authorization request. | Yes |  |  |  | X | [16 empty] | X
123 | Prior to commencement of service, Commonwealth shall provide plans for any preventative and predictive maintenance program that performs periodic or continuous equipment condition monitoring. | Technip | Owner | Technip shall provide plans for any preventative and predictive maintenance program that performs periodic or continuous equipment condition monitoring. | Owner to reference Condition in Commencement of Service authorization request. | Yes | [22 empty] | X |  | X | X
124 | Prior to commencement of service, Commonwealth shall develop procedures for offsite contractors’ responsibilities, restrictions, monitoring, training, and limitations and for supervision of these contractors and their tasks by Commonwealth staff. Specifically, the procedures shall address: a. selecting a contractor, including obtaining and evaluating information regarding the contract employer’s safety performance and programs; b. informing contractors of the known potential hazards, including flammable and toxic release, explosion, and fire, related to the contractor's work and systems they are working on; c. developing and implementing provisions to control and monitor the entrance, presence, and exit of contract employers and contract employees from process areas, buildings, and the plant; d. developing and implementing safe work practices for control of personnel safety hazards, including lockout/tagout, confined space entry, work permits, hot work, and opening process equipment or piping; e. developing and implementing safe work practices for control of process safety hazards, including identification of layers of protection in systems being worked on, recognizing abnormal conditions on systems they are working on, and re-instatement of layers of protection, including ensuring bypass, isolation valve, and car-seal programs and procedures are being followed f. developing and implementing provisions to ensure contractors are trained on the emergency action plans and that they are accounted for in the event of an emergency; and g. monitoring and periodically evaluating the performance of contract employers in fulfilling their obligations above, including successful and safe completion of work and re-instatement of all layers of protection. | Owner | NA | None | Owner to reference Condition in Commencement of Service authorization request. | No | X
125 | The facility shall be subject to regular FERC staff technical reviews and site inspections on at least an annual basis or more frequently as circumstances indicate. Prior to each FERC staff technical review and site inspection, Commonwealth shall respond to a specific data request including information relating to possible design and operating conditions that may have been imposed by other agencies or organizations. Up-to-date detailed P&IDs reflecting facility modifications and provision of other pertinent information not included in the semiannual reports described below, including facility events that have taken place since the previously submitted semi-annual report, shall be submitted. | Owner | Technip | Technip shall support Owner during construction and commissioning inspections as required. Technip would support Owner with Operations inspections only if there are open mitigation measures that were not satisfied after Owner receives In-Service authorization or for any other reasons under the EPC Agreement. | Life of Facility Condition for Owner to file compliance statement in General Conditions Implementation Plan. Includes response to specific data request on possible design and operation conditions imposed by other agencies. | No | X
126 | Semi-annual operational reports shall be filed with the Secretary to identify changes in facility design and operating conditions; abnormal operating experiences; activities (e.g., ship arrivals, quantity and composition of imported and exported LNG, liquefied and vaporized quantities, boil off/flash gas); and plant modifications, including future plans and progress thereof. Abnormalities shall include, but not be limited to, unloading/loading/shipping problems, potential hazardous conditions from offsite vessels, storage tank stratification or rollover, geysering, storage tank pressure excursions, cold spots on the storage tank, storage tank vibrations and/or vibrations in associated cryogenic piping, storage tank settlement, significant equipment or instrumentation malfunctions or failures, nonscheduled maintenance or repair (and reasons therefore), relative movement of storage tank inner vessels, hazardous fluids releases, fires involving hazardous fluids and/or from other sources, negative pressure (vacuum) within a storage tank, and higher than predicted boil off rates. Adverse weather conditions and the effect on the facility also shall be reported. Reports shall be submitted within 45 days after each period ending June 30 and December 31. In addition to the above items, a section entitled “Significant Plant Modifications Proposed for the Next 12 Months (dates)” shall be included in the semi-annual operational reports. Such information would provide the FERC staff with early notice of anticipated future construction/maintenance at the LNG facilities. | Owner | NA | None | Life of Facility Condition for Owner. Owner to file semiannual operational reports. Owner will also file compliance statement with General Conditions Implementation Plan. Includes abnormalities and planned schedule modifications proposed next 12 months. | No | X
127 | In the event the temperature of any region of the LNG storage container, including any secondary containment and imbedded pipe supports, becomes less than the minimum specified operating temperature for the material, the Commission shall be notified within 24 hours and procedures for corrective action shall be specified. | Owner | Technip | Technip shall support Owner as required after LNG is introduced into LNG Storage Tank until Technip responsibility ends as defined in the EPC Agreement. | Life of Facility Condition for Owner. Owner to notify FERC within 24 hours. Owner will file compliance statement in General Conditions Implementation Plan. | No | X
128 | Significant non-scheduled events, including safety-related incidents (e.g., LNG, condensate, refrigerant, or natural gas releases; fires; explosions; mechanical failures; unusual over pressurization; and major injuries) and security-related incidents (e.g., attempts to enter site, suspicious activities) shall be reported to the FERC staff. In the event that an abnormality is of significant magnitude to threaten public or employee safety, cause significant property damage, or interrupt service, notification shall be made immediately, without unduly interfering with any necessary or appropriate emergency repair, alarm, or other emergency procedure. In all instances, notification shall be made to the FERC staff within 24 hours. This notification practice shall be incorporated into the liquefaction facility’s emergency plan. Examples of reportable hazardous fluids-related incidents include: a. fire; b. explosion; c. estimated property damage of $50,000 or more; d. death or personal injury necessitating in-patient hospitalization; e. release of hazardous fluids for 5 minutes or more; f. unintended movement or abnormal loading by environmental causes, such as an earthquake, landslide, or flood, that impairs the serviceability, structural integrity, or reliability of an LNG facility that contains, controls, or processes hazardous fluids; g. any crack or other material defect that impairs the structural integrity or reliability of an LNG facility that contains, controls, or processes hazardous fluids; h. any malfunction or operating error that causes the pressure of a pipeline or LNG facility that contains or processes hazardous fluids to rise above its maximum allowable operating pressure (or working pressure for LNG facilities) plus the build-up allowed for operation of pressure-limiting or control devices; i. a leak in an LNG facility that contains or processes hazardous fluids that constitutes an emergency; j. inner tank leakage, ineffective insulation, or frost heave that impairs the structural integrity of an LNG storage tank; k. any safety-related condition that could lead to an imminent hazard and cause (either directly or indirectly by remedial action of the operator), for purposes other than abandonment, a 20 percent reduction in operating pressure or | Owner | Technip | Technip shall support Owner throughout Project until their responsibility ends as defined in the EPC Agreement. | Life of Facility Condition for Owner. Owner to notify FERC immediately or within 24 hours. Owner to file compliance statement in General Conditions Implementation Plan. | No | X | [19 empty] | S

## Sheet1 (hidden)
Drop downlist 1 | Drop downlist 2
HOC | Yes
POC | No
HOC/POC - Geographical split
N/A

## FEIS (hidden)
Condition | Condition Statement | Adder | Primary Responsibility | Secondary Responsibility | Department | is | Owner Condition Compliance Responsibilites | Comments | Resolution | TQ # 1000-2000 | Action | Technip Response | Status
1 | Commonwealth LNG, LLC (Commonwealth) shall follow the construction procedures and mitigation measures described in its application and supplements, including responses to staff data requests and as identified in the EIS, unless modified by the Order. Commonwealth must: a. request any modification to these procedures, measures, or conditions in a filing with the Secretary of the Commission (Secretary); b. justify each modification relative to site-specific conditions; c. explain how that modification provides an equal or greater level of environmental protection than the original measure; and d. receive approval in writing from the Director of the Office of Energy Projects (OEP), or the Director’s designee, before using that modification. | No | Owner | Technip | All | Technip to provide comments regarding modifications of procedures, measures or conditions, justify modifications described in application, supplements, data requests and EIS. | Owner to file Variance Requests for approval to FERC. | Must follow the plan. Change orders need to be assessed and approved by the Director of OEP PDN system is up and running to track engineering changes | this is an ongoing process. PDN system has been rolled out to track these items. DWGs and specs will be flagged with the change and eventual work packs created to send to CWLNG to send to FERC. |  | General Conditions
2 | The Director of OEP, or the Director’s designee, has delegated authority to address any requests for approvals or authorizations necessary to carry out the conditions of the Order, and take whatever steps are necessary to ensure the protection of life, health, property, and the environment during construction and operation of the Commonwealth LNG Project (Project). This authority shall allow: a. the modification of conditions of the Order; b. stop-work authority and authority to cease operation; and c. the imposition of any additional measures deemed necessary to ensure continued compliance with the intent of the conditions of the Order as well as the avoidance or mitigation of unforeseen adverse environmental impacts resulting from Project construction and operation. | No | Owner | Technip | HSE | Technip to provide documentation and comply with FERC directives as necessary (with Owner guidance) if the Director of OEP utilizes their delegated authority as detailed in Condition. | Owner to file Compliance Statement with FERC in General Conditons Implementation Plan. | Director of OEP can stop work and ensure FERC recommendations are being followed | ongoing supervision throughout the project |  | General Conditions
3 | Prior to any construction, Commonwealth shall file an affirmative statement with the Secretary, certified by senior company officials, that all company personnel, environmental inspectors (EI), and Technip personnel will be informed of the EI’s authority and have been or will be trained on the implementation of the environmental mitigation measures appropriate to their jobs before becoming involved with construction and restoration activities. | No | Owner | Technip | HSE | Technip to ensure their personnel and contractors have been trained on the implementation of the envirnomental mitiagation measures appropriate to their jobs before becoming involved with construction and restoration activities. | Owner to file affirmative statement with FERC in General Conditons Implementation Plan and ensure compliance with statement. |  |  |  | General Conditions
4 | The authorized facility locations shall be as shown in the EIS, as supplemented by filed plot plans, alignment sheets, and facility diagrams. As soon as they are available, and before the start of construction, Commonwealth shall file with the Secretary any revised detailed plans, diagrams, and alignment sheets at a scale not smaller than 1:6,000 with station positions for all facilities approved by the Order. All requests for modifications of environmental conditions of the Order or site-specific clearances must be written and must specify locations designated on these plans, diagrams, and alignment sheets. | No | Owner | Technip | Piping | Technip to provide revised detailed plans, diagrams and alignment sheets for revisions to the authorized facility locations shown in the EIS. | Owner to file revised detailed plans, diagrams and alignments sheets for approval to FERC. |  | plot plans are and DWGs are being updated with new info all the time needs to be submitted to FERC in the new submittal |  | General Conditions
5 | Commonwealth shall file with the Secretary detailed alignment maps/sheets and aerial photographs at a scale not smaller than 1:6,000 identifying all route realignments or facility relocations, and staging areas, pipe storage yards, new access roads, and other areas that would be used or disturbed and have not been previously identified in filings with the Secretary. Approval for each of these areas must be explicitly requested in writing. For each area, the request must include a description of the existing land use/cover type, documentation of landowner approval, whether any cultural resources or federally listed threatened or endangered species would be affected, and whether any other environmentally sensitive areas are within or abutting the area. All areas shall be clearly identified on the maps/sheets/aerial photographs. Each area must be approved in writing by the Director of OEP before construction in or near that area. This requirement does not apply to extra workspace allowed by the Commission’s Upland Erosion Control, Revegetation & Maintenance Plan and/or minor field realignments per landowner needs and requirements which do not affect other landowners or sensitive environmental areas such as wetlands. Examples of alterations requiring approval include all route realignments and facility location changes resulting from: a. implementation of cultural resources mitigation measures; b. implementation of endangered, threatened, or special concern species mitigation measures; c. recommendations by state regulatory authorities; and d. agreements with individual landowners that affect other landowners or could affect sensitive environmental areas. | No | Owner | Technip | Piping | Technip to provide alignment maps/sheets and aerial photographs for route alignments, facility relocations, staging areas, pipe storage yards, new access roads and other areas that would be used or disturbed and have not been previously identified in filings. | Owner to file with FERC in General Condition Implementation Plan any revisions to the route or facility relocations, staging areas, pipe storage yards, new access roads or other areas not previously identified in filings for approval to FERC. | Company (with support from TEN) to file overall plot plan with the Secretary showing any construction support areas that were not part of the FERCA submission | Information gathered from TEN issued documentation to be sent to FERC in next submission |  | General Conditions
6 | At least 60 days before construction begins, Commonwealth shall each file an Implementation Plan with the Secretary, for review and written approval by the Director of OEP. Commonwealth must file revisions to the plans as schedules change. The plans shall identify the following: a. how Commonwealth will implement the construction procedures and mitigation measures described in its application and supplements (including responses to staff data requests), identified in the EIS, and required by the Order; b. how Commonwealth will incorporate these requirements into the contract bid documents, construction contracts (especially penalty clauses and specifications), and construction drawings so that the mitigation required at each site is clear to onsite construction and inspection personnel; c. the number of EIs assigned per spread and aboveground facility sites, and how the company will ensure that sufficient personnel are available to implement the environmental mitigation; d. company personnel, including EIs and contractors, who will receive copies of the appropriate material; e. the location and dates of the environmental compliance training and instructions Commonwealth will give to all personnel involved with construction and restoration (initial and refresher training as the project progresses and personnel change), with the opportunity for OEP staff to participate in the training session(s); f. the company personnel (if known) and specific portion of Commonwealth’s organization having responsibility for compliance; g. the procedures (including use of contract penalties) Commonwealth will follow if noncompliance occurs; and i. for each discrete facility, a Gantt or PERT chart (or similar project scheduling diagram), and dates for: ii, the completion of all required surveys and reports; iii. the environmental compliance training of onsite personnel; iv. the start of construction; and v. the start and completion of restoration. | No | Owner | Technip | PM | Technip to provide updates to schedule, how construction procedures will be implemented, Organizational chart for environmental responsiblity to provide copies of environmental documents, environmental training records available on an as-needed basis. Requirements in the contract bid, construction contracts and construction drawings so that mitigation at each site is clear to onsite construction and inspection personnel. | Owner to file in the General Condition Implementation Plan construction procedures, mitigation measures, identify how EIs assigned and sufficient personnell to implement mitigation, compliance training, organizational compliance responsbility, and contract penalties if noncompliance occurs. | Company to use TEN schedules to gather info and send to FERC |  |  | General Conditions
7 | Commonwealth shall employ at least one EI for the Project. The EI(s) shall be: a. responsible for monitoring and ensuring compliance with all mitigation measures required by the Order and other grants, permits, certificates, or other authorizing documents; b. responsible for evaluating the construction contractor's implementation of the environmental mitigation measures required in the contract (see condition 6 above) and any other authorizing document; c. empowered to order correction of acts that violate the environmental conditions of the Order, and any other authorizing document; d. a full-time position, separate from all other activity inspectors; e. responsible for documenting compliance with the environmental conditions of the Order, as well as any environmental conditions/permit requirements imposed by other federal, state, or local agencies; and f. responsible for maintaining status reports. | No | Owner | Technip |  | Technip acknowledges that the EI(s) is responsible for evaluating the the construction contractor's implementation of the environmental mitigation measures required in the contract and is empowered to order correction of acts that violate the environmental conditions of the Order and any other authorizing document. Will provide environmental status updates to Owner on a weekly basis. | Owner to file Compliance Statement and responsible for status reports with FERC in General Conditons Implementation Plan. | Company employee |  |  | General Conditions
8 | Beginning with the filing of its Implementation Plan, Commonwealth shall file updated status reports with the Secretary on a monthly basis until all construction and restoration activities are complete. Problems of a significant magnitude shall be reported to the FERC within 24 hours. On request, these status reports will also be provided to other federal and state agencies with permitting responsibilities. Status reports shall include the following: a. an update on Commonwealth's efforts to obtain the necessary federal authorizations; b. project schedule including the current construction status and work planned for the following reporting period; c. listing of all problems encountered, Technip nonconformance/deficiency logs, and each instance of noncompliance observed by the EIs during the reporting period (both for the conditions imposed by the Commission and any environmental conditions/permit requirements imposed by other federal, state, or local agencies); d. a description of the corrective and remedial actions implemented in response to all instances of noncompliance, nonconformance, or deficiency; e. the effectiveness of all corrective and remedial actions implemented; f. a description of any landowner/resident complaints which may relate to compliance with the requirements of the Order, and the measures taken to satisfy their concerns; and g. copies of any correspondence received by Commonwealth from other federal, state, or local permitting agencies concerning instances of noncompliance, and Commonwealth’s response. | No | Owner | Technip |  | Technip to provide status report that include construction status and work planned, noncompliances and actions taken to remedy. | Owner to file Compliance Statement with FERC in General Conditons Implementation Plan and will file updated status reports that includes noncompliances, remedies, and resolution, effectiveness of actions and landowner issues with agency correspondence recevied and file on a monthly basis or within 24 hours for problems of a significant magnitude. | Monthly updates to the Secretary and notification of major changes |  |  | General Conditions
9 | Commonwealth shall develop and implement an environmental complaint resolution procedure, and file such procedure with the Secretary, for review and approval by the Director of OEP, or the Director’s designee. The procedure shall provide landowners with clear and simple directions for identifying and resolving their environmental mitigation problems/concerns during construction of the project and restoration of the right-of-way. Prior to construction, Commonwealth shall mail the complaint procedures to each landowner whose property will be crossed by the project. a. In its letter to affected landowners, Commonwealth shall: i. provide a local contact that the landowners should call first with their concerns; the letter should indicate how soon a landowner should expect a response; ii. instruct the landowners that if they are not satisfied with the response, they should call Commonwealth's Hotline; the letter should indicate how soon to expect a response; and iii. instruct the landowners that if they are still not satisfied with the response from Commonwealth's Hotline, they should contact the Commission’s Landowner Helpline at 877-337-2237 or at LandownerHelp@ferc.gov. b. In addition, Commonwealth shall include in its monthly status report a copy of a table that contains the following information for each problem/concern: i. the identity of the caller and date of the call; i. the location by milepost and identification number from the authorized alignment sheet(s) of the affected property; ii. a description of the problem/concern; and iii. an explanation of how and when the problem was resolved, will be resolved, or why it has not been resolved. | No | Owner | NA |  | None | Owner to develop the complaint resolution procedure with FERC prior to construction. Owner will also mail the procedures to each landowner whose property that will be crossed by project and implement complaint procedures prior to construction. |  |  |  | General Conditions
10 | All conditions attached to the water quality certification issued by Louisiana Department of Environmental Quality constitute mandatory conditions of this Authorization Order. Prior to construction, Commonwealth shall file, for review and written approval of the Director of OEP, or the Director’s designee, any revisions to its project design necessary to comply with the water quality certification conditions. | No | Owner | Technip |  | Technip to provide supporting documents to Owner for any revisions to the project design necessary to comply with the LDEQ water quality certification conditions. | Owner to file WQC and as relevant project design revisions as required. |  |  |  | General Conditions
11 | Commonwealth must receive written authorization from the Director of OEP before commencing construction of any Project facilities. To obtain such authorization, Commonwealth must file with the Secretary documentation that it has received all applicable authorizations required under federal law (or evidence of waiver thereof). | No | Owner | NA |  | None | Owner to file Compliance Statement and updated Permits Table with FERC in General Conditions Implementation Plan. |  |  |  | General Conditions
12 | Commonwealth must receive written authorization from the Director of OEP prior to introducing hazardous fluids into the LNG Facility. Instrumentation and controls, hazard detection, hazard control, and security components/systems necessary for the safe introduction of such fluids shall be installed and functional. | No | Owner | Technip |  | Technip to provide supporting documentation as required and ensure that instrumentation and controls, hazard detection, hazard control, and security components/systems necessary for the safe introduction of such fluids shall be installed and functional. | Owner to file Compliance Statement with FERC in General Conditions Implementation Plan and will file request to introduce hazardous fluids into the LNG Facility when appropriate. |  |  |  | General Conditions / Hazardous Fluids
13 | Commonwealth must receive written authorization from the Director of OEP, or the Director’s designee, before placing into service the Project facilities. Such authorization will only be granted following a determination that the facilities have been constructed in accordance with FERC approval, can be expected to operate safely as designed, and the rehabilitation and restoration of areas affected by the project are proceeding satisfactorily. | No | Owner | Technip |  | Technip to ensure that the Project facilities are constructed in accordance with FERC approval and to operate safely as designed. Technip to provide status of site rehabilitation and restoration. | Owner to file Compliance Statement with FERC in General Conditions Implementation Plan and will file request to place Project facilities into service when appropriate. |  |  |  | General Conditions / Commence Service
14 | Within 30 days of placing the authorized facilities in service, Commonwealth shall file an affirmative statement with the Secretary, certified by a senior company official: a. that the facilities have been constructed in compliance with all applicable conditions, and that continuing activities will be consistent with all applicable conditions; or b. identifying which of the conditions in the Order Commonwealth has complied with or will comply with. This statement shall also identify any areas affected by the Project where compliance measures were not properly implemented, if not previously identified in filed status reports, and the reason for noncompliance. | No | Owner | Technip |  | Technip to support Owner as necessary if there are any conditions not yet satisfied or compliance measures not properly implemented at the time the authorized facilites are place in service. | Owner to file Compliance Statement with FERC in General Conditions Implementation Plan and will file affirmative statement certified by senior company offical within 30 days of placing the authorized facilities into service. |  |  |  | General Conditions / Commence Service
15 | Prior to construction of the Project Pipeline, Commonwealth shall file with the Secretary for review and written approval by the Director of OEP, or the Director’s designee, an alternative contingency plan for crossing Highway 27/82 in the event that Commonwealth is unable to successfully complete the proposed horizontal directional drill of Highway 27/82. Commonwealth shall develop the contingency plan in consultation with the Louisiana Department of Transportation and Development. | No | Owner | NA |  | None | Owner has sole responsibility for Project Pipeline and will file compliance with FERC prior to construction of the Project Pipeline if contingency plan is required. |  |  |  | General Conditions / Pipeline
16 | Commonwealth shall successfully complete the Highway 27/82 crossing prior to the start of construction of the remainder of the Project Pipeline. | No | Owner | NA |  | None | Owner has sole responsibility for Project Pipeline and will reference Condition prior to the start of construction of the remainder of the Project Pipelien. |  |  |  | General Conditions / Pipeline
17 | Prior to construction of the Project, Commonwealth shall file with the Secretary a copy of the determination of consistency with the Coastal Zone Management Program issued by the Louisiana Department of Natural Resources. | No | Owner | Technip |  | Technip to support Owner as necessary, if changes occur to impact CZM. | Owner to file Compliance Statement and determination of consistency with FERC in General Conditions Implementation Plan. |  |  |  | General Conditions
18 | During construction activities at the Terminal, Commonwealth shall monitor noise levels between 7:00 p.m. and 7:00 a.m., document the noise levels in the construction status reports, and restrict the noise attributable to construction activities to no more than 55 A-weighted decibel (dBA) day-night sound level (Ldn) (48.6 dBA total noise impacts) at noise sensitive areas (NSA) 1 and 2. | No | Technip | Owner |  | Technip to monitor noise levels between 7:00 p.m. and 7:00 a.m. during construction activities at the Terminal and restrict noise levels attributale to construction activities as proscribed in Condition. Technip to provide levels to Owner who will include in construction status reports. | Owner to document in construction status reports filed with FERC. |  |  |  | General Conditions
19 | Commonwealth shall file a full power load noise survey with the Secretary for the Terminal no later than 60 days after each liquefaction train is placed into service. If the noise attributable to operation of the equipment at the Terminal exceeds an Ldn of 55 dBA at NSAs, within 60 days Commonwealth shall modify operation of the liquefaction facilities or install additional noise controls until a noise level below an Ldn of 55 dBA at the NSAs is achieved. Commonwealth shall confirm compliance with the above requirement by filing a second noise survey with the Secretary no later than 60 days after it installs the additional noise controls. | No | Owner | Technip |  | Technip to provide Owner with noise survey data for each liquefaction train and make modifications or install additional noise controls as necessary if noise levels exceed authorized levels. | Owner to file Compliance Statement with FERC in General Conditions Implementation Plan and will file noise surveys with FERC after each liquefaction train is placed into service. |  |  |  | General Conditions / Commence Service
20 | Commonwealth shall file a noise survey with the Secretary no later than 60 days after placing the entire Terminal into service. If a full load condition noise survey is not possible, Commonwealth shall provide an interim survey at the maximum possible horsepower load within 60 days of placing the Terminal into service and provide the full load survey within 6 months. If the noise attributable to operation of the equipment at the Terminal exceeds an Ldn of 55 dBA at any nearby NSA under interim or full horsepower load conditions, Commonwealth shall file a report on what changes are needed and shall install the additional noise controls to meet the level within 1 year of the in-service date. Commonwealth shall confirm compliance with the above requirement by filing an additional noise survey with the Secretary no later than 60 days after it installs the additional noise controls. | No | Owner | Technip |  | Technip to provide Owner with noise survey data for entire Terminal and make modifications or install additional noise controls as necessary if noise levels exceed authorized levels. | Owner to file Compliance Statement with FERC in General Conditions Implementation Plan. Owner will file noise surveys with FERC no later than 60 days after placing the entire Terminal into service, operation less than 55 dBA at the NSA. |  |  |  | General Conditions / Commence Service
21 | Prior to initial site preparation, Commonwealth shall file with the Secretary the following information, stamped and sealed by the professional engineer-of-record, registered in the State of Louisiana: a. finalized ground improvement solution of wick drains combined with surcharge for the Project site; b. site soil compaction via surcharge procedures and specifications; and c. finalized wick drains installation design package. | No | Technip | Owner |  | Technip to provide PE stamped and sealed information for items a, b anc c. | Owner will review, format as necessary and file with FERC in Site Preparation Implementation Plan. | paperwork filing wick drains are under design Earthwork & Wick Drain Plan = 078051C-0000-DW-1423-0004-1 SUBCONTRACT SCOPE OF WORK FOR SPECIFIC ACTIVITIES SITE PREPARATION WORKS = 078051C-000-SOW-1420-0001 | T.EN released the second round of the site preparation package on 10-28-22. This package contains a) the proposed ground improvement solution of wick drains combined with surcharge, b) procedures and specifications, and c) wick drain installation design package. Once the comments to the second round of the site preparation package be incorporated, T.EN will publish the package Issue for Review in GAIA, and then Issue for Construction in GAIA also. This last step will contain the drawings and main document signed and stamped by a Louisiana Professional Engineer. The next step will be file the site preparation package to FERC. | 1001 | Site Prep. | T.EN released the PE stamped version of site prep drawings/documents before Nov, 2023 for FERC submission. The latest/Final version of these drawings/documents will be available by the end of EB2
22 | Prior to initial site preparation, Commonwealth shall file with the Secretary the following information, stamped and sealed by the professional engineer-of-record, registered in the State of Louisiana: a. the corrosion control and prevention plan for any underground piping, structures, foundations, equipment, and components; and b. the erosion control and prevention plan for the marine facility area. | No | Technip | Owner |  | Technip to provide PE stamped and sealed information for items a and b. | Owner will review, format as necessary and file with FERC in Site Preparation Implementation Plan. | paperwork filing This action needs to be reclassified to "Corrosion/Coating" and "Marine" Departments. Erosion and Sediment Control Plan = 078051C-0100-DW-1423-0003 Erosion and Sediment Control Measures-Standard Silt Fence and Construction Exit = 078051C-000-STD-1480-0036 | A. will be in the marine subcontractors SOW. The only underground components of the Marine Facilities will be piles in the LNGC Berth. The plan is that the underground portions of the piles will be uncoated from ten feet below design grade to their tips and will be protected by the dedicated impressed current cathodic protection system (ICCP) on the LNGC berth. B. there is nothing in the Marine Facilities SOW that is uplands (interface points with shore is a bulkhead provided by Onshore Contractor and the rip rap section designed to prevent erosion) thus no draft SWPPP or other erosion control is required. FEIS specifically is asking about prop wash on clay slopes SOW will require Subcontractor to install permanent scour protection on slopes of basin not immediately in way of LNGC Berth piling as soon as dredging in that location is completed. (for example in front of the MORAN tug berths, the MOF, and the southern dredge basin fillet to deep water) The only slope that will not be protected within a month of creation during Marine Subcontractor activities will be the slopes the Subcontractor is actively working on. Note the materials at site – especially those below -15 NGVD88 – are not particularly erodible. |  | Site Prep. | T.EN released the PE stamped version of site prep drawings/documents before Nov, 2023. The latest/Final version of these drawings/documents will be available by the end of EB2 To be checked with CWLNG FERC rep about the requirement of Marine Subcon execution documents.
23 | Prior to initial site preparation, Commonwealth shall file with the Secretary the finalized plot plan with final design of finished slopes and elevations contour lines for the Project site. The finalized plot plan shall be stamped and sealed by the professional engineer-of-record, registered in the State of Louisiana. | No | Technip | Owner |  | Technip to provide PE stamped and sealed finalized plot with final design of finished slopes and elevation contours for the Project site. | Owner will review, format as necessary and file with FERC in Site Preparation Implementation Plan. | plot plan is always being updated Overall Plot Plan = 078051C-0000-DW-0051-0002 Site Preparation - Rough Grading Plan - Sheet 1-3 = 1078051C-0100-DW-1421-0001-1, 2, 3 Earthwork & Wick Drain Plan = 078051C-0000-DW-1423-0004-1, 2, 3 Overall Site and Demolition Plan = 078051C-0100-DW-1423-0002-1, 2 | The final plot plan with final design of finish slopes and elevation contour will be included into the Site Preparation Package. See Item # 21 for further details. | 1002 | Site Prep. | T.EN released the PE stamped version of Plot Plan before Nov, 2023 for FERC submission.. Further to be discussed with CWLNG on the
24 | Prior to initial site preparation, Commonwealth shall file with the Secretary the finalized pile load test program (e.g., pile load test procedure, locations, configuration, quality assurance, and quality control, etc.). The filing shall be stamped and sealed by the professional engineer-of-record, registered in the State of Louisiana. | No | Technip | Owner |  | Technip to provide PE stamped and sealed finalized pile load test program. | Owner will review, and file with FERC in Site Preparation Implementation Plan. | The pile contractor will design the piles and confirm the pile load test program to be used and as scheduled. Pile load test program and piling activities cannot start until after completion of site prep and soil consolidation. Conducting a pile load test on the site prior to site prep and soil consolidation will provide incorrect assessment of the pile performance. Therefore we want to move the timing of the pile load test program prior to the start of piling operations | This will not be available as the site prep contractor is responsible for the pile design and they will not have the design completed before the start of site prep. Once T.EN finalize some discussions regarding the best type of pile for the project, we will prepare the finalized Pile Load Test Program, including but not limited to procedures, locations, configurations, quality assurance and quality control, among others. The document will be signed and stamped by a Louisiana Professional Engineer. |  | Site Prep. | This is a deliverable by Piling Subcontractor and will be available after the contractor is onboarded - To be discussed with SubcontRacts on the timeline 03/26/25 - This will be further discussed with FERC rep from TEN and CWLNG for better clarity on the PE stamping and requirement of the documents from Subcon/TEN CSA.
25 | Prior to site initial preparation, Commonwealth shall file with the Secretary the final design of floodwalls (storm surge protection barriers) to comply with applicable code/standards requirements including but are not limited to National Fire Protection Association (NFPA) 59A (2019 edition) as incorporated by 33 Code of Federal Regulations (CFR) 127, and NFPA 59A (2001 edition) in 49 CFR 193. In addition, the floodwalls shall be designed and maintained in accordance with American Society of Civil Engineers (ASCE)/Structural Engineering Institute (SEI) 7 (2022 edition) or equivalent and ASCE/SEI 24 (2014 edition) or equivalent and to withstand a minimum of a 500-year mean occurrence interval in consideration of relative sea level rise, local subsidence, site settlement, shoreline recession, erosion and scour effect, and wind-driven wave effects, etc. The sea level rise and vertical land movement should be in accordance with at a minimum intermediate curve corresponding to design life of facility in Global and Regional Sea Level Rise Scenarios for the United States. U.S. Department of Commerce. National Ocean and Atmospheric Administration, National Ocean Service Center for Operational Oceanographic Products and Services, February 2022 or equivalent. The final design of floodwalls shall be stamped and sealed by the professional engineer-of-record, registered in the State of Louisiana. | No | Technip | Owner |  | Technip to provide PE stamped and sealed final design of floodwalls (storm surge protection barriers). Technip will also be designed and maintain the floodwalls (per the applicable codes) per the terms of the EPC Agreement. In accordance with intermediate curve in Global and Regional Sea Level Rise Scenarios for the US. | Owner will review, format as necessary and file with FERC in Site Preparation Implementation Plan. Floodwall design may be filed in Site Preparation supplmental filing if final design is not completed at the time of the Site Preparation filing but only if approach is approved by FERC. | Metocean report will not be completed until late Dec and the design will not be finalized before the projected start time of the site prep. need to ask for a varience. | T.EN is currently working on the first draft of the Surge Floodwall Design Scope of Work. This document will be released around 11-07-22. This document will address the the requirements to design the surge floodwall per a) NFPA 59A (2019 Edition) standard per 33 CFR 127, b) NFPA 59A (2001 Edition) per CFR 193, c) ASCE/SEI 7-22 or equivalent, and d) ASCE/SEI 24 (2014 Edition), among others to withstand a minimum of a 500-year mean occurrence interval in consideration of relative sea level rise, local subsidence, site settlement, shoreline recession, erosion and scour effect, and wind-driven wave effects, etc. The drawings and main documents will be signed and stamped by a Louisiana Professional Engineer. 1) Storm Surge Wall design – completion of the design is dependent upon the revised Coastal Climatology Report which is currently being performed. The initial Coastal Climatology report was reviewed as part of continued engineering design and found to have gaps that needed to be addressed. Completion of the revised Coastal Climatology Report is expected in December 2022, however this revised report is a critical input to the Storm Surge Wall Design. Storm Surge Wall Design is estimated to require 8-9 months to complete, including: a. development of the design scope of work requirements (2-4 weeks), b. solicitation of bids from qualified suppliers (4-6 weeks), c. bid review and award placement (2-4 weeks), and d. actual engineering design activities (6 months) Therefore, the design will not be completed before the proposed start of site prep. 2) Construction of the Storm Surge Wall is planned after the completion of site prep, soil consolidation, and piling installation. These preparatory activities will not be completed until at least Q1 of 2024, by which time the design of the storm surge wall will be complete. 3) General Early Works Schedule: a. Receive FERC Permit – Q4 2022 b. Received revised Coastal Climatology Report – Q4 2022 c. Start Site Prep Activities – Q2 2023 d. Complete Storm Surge Wall design – Q3 2023 e. Construction of Storm Surge Wall – Q2 2024 |  | Site Prep. | T.EN released the PE stamped version of floodwalls (storm surge protection barriers)/documents before , 2024. To be checked with Marissa
26 | Prior to construction of final design, Commonwealth shall file with the Secretary consultation with U.S. Department of Transportation’s (DOT) Pipeline and Hazardous Materials Safety Administration (PHMSA) that determines whether the use of normally closed valves to remove stormwater from curbed areas will meet PHMSA regulations. | No | Owner | Technip |  | Technip to provide documentation and support as necessary to support Owner consultation with DOT PHMSA. Stormwater removal system must comply with PHMSA regulations. | Owner will consult with DOT PHMSA and will file consultation with FERC prior to construction of final design of curbed areas. | paperwork filing This action needs to be reclassified to "Fire & Safety" or "Process Safety" or "HSE" Departments. This is a Process item. |  |  | Spill Cont. Systems
27 | Prior to construction of final design, Commonwealth shall file with the Secretary the following information, stamped and sealed by the professional engineer-of-record, registered in the State of Louisiana: a. the finalized settlement monitoring program and procedures for the Project site; b. the total and differential settlement of final designed structures, systems, and components foundations for the Project site; and c. the total and differential settlement monitoring system of LNG storage tank foundation design shall comply with applicable LNG industrial codes/standards, including but not limited to American Petroleum Institute (API) 620 (12th edition), API 625 (1st edition), API 650 (13th edition), API 653 (5th edition), and ACI 376 (2011 edition) or approved equivalents. | No | Technip | Owner |  | Technip to provide PE stamped and sealed information for items a, b and c. | Owner will review, format as necessary and file with FERC in the appropriate Final Design Implementation Plans. |  | T.EN prepared and released to bidder the subcontract "Additional Geotechnical Scope of Work", which contains the task 5.1 "Field Settlement Monitoring Program", including settlement maintenance plan. This item addresses the topic of the Actions 27 and 30. This document will be signed and stamped by a Louisiana Professional Engineer. ( PE stamping on documents is under Tank Subcontractor's responsibility). |  | Piling Foundations / LNG Tanks
28 | Prior to construction of final design, Commonwealth shall file with the Secretary the following information, stamped and sealed by the professional engineer-of-record, registered in the State of Louisiana: a. site preparation drawings and specifications; b. finalized civil design basis, criteria, specifications; c. LNG terminal structures, LNG storage tank, and foundation design drawings and calculations (including prefabricated and field constructed structures); d. seismic specifications for procured Seismic Category I equipment prior to the issuing of request for quotations; e. quality control procedures to be used for civil/structural design and construction; and f. a determination of whether soil improvement is necessary to counteract soil liquefaction. In addition, Commonwealth shall file, in its Implementation Plan, the schedule for producing this information. | No | Technip | Owner |  | Technip to provide PE stamped and sealed information for items a-f. Technip will provide a schedule for producing the deliverables identified in a-f. | Owner will review, format as necessary and file with FERC in the appropriate Implementation Plans. Items a, b, e, and f to be schedule for producing will be filed with Site Preparation Implementation Plan. Items c and d to be filed in appropriate Final Design Implementation Plans. |  | T.EN is working on the preparation of these documents as follow: a) Site Preparation drawings and specifications: In progress. See Item # 21 above. b) Civil strucural design basis, criteria and specifications: In progress by T.EN. c) LNG terminal structures, tank and foundation: In progress by Arup. d) Seismic specifications: In progress. The seismic specifications are included on item b) above. e) Quality control procedures: To be prepared by T.EN. f) No liquefaction is expected according to the soil report. T.EN will write a letter or report establishing this comment. |  | Site Prep. / Piling Foundations / Structures / LNG Tanks | a. site preparation drawings and specifications; - T.EN released the PE stamped version of site prep drawings/documents before Nov, 2023 for FERC submission. The latest/Final version of these drawings/documents will be released by TEN by the end of EB2 b. finalized civil design basis, criteria, specifications; - Rev 2 was provided to FERC along with clarifications on the categoric queries raised by FERC in 2024. c. LNG terminal structures, LNG storage tank, and foundation design drawings and calculations (including prefabricated and field constructed structures); - LNG Tank documents will be part of LNG Subcontractor Engineering documents and will be available in the EPC stage of the project along with LNG Terminal Structures documents which will also be issued by TEN during EPC stage of the Project. d. seismic specifications for procured Seismic Category I equipment prior to the issuing of request for quotations; - This is part of civil design basis Rev 2. e. quality control procedures to be used for civil/structural design and construction; and - 03/26/25 - This will be further discussed with FERC rep from TEN and CWLNG for better clarity on the requirement of the documents from Subcon/TEN Const. Civil Subcon documents will be available in 2026. f. a determination of whether soil improvement is necessary to counteract soil liquefaction. In addition, Commonwealth shall file, in its Implementation Plan, the schedule for producing this information. - Soil improvement is required to improve the consolidation of ground. No liquefaction is expected per Rev 2 of the Geotechnical report by Thompson Engineering.
29 | Prior to construction of the final design, Commonwealth shall file with the Secretary the finalized seismic monitoring program for the Project site. The seismic monitoring program shall comply with NFPA 59A (2019 edition) sections 8.4.14.10, 8.4.14.12, 8.4.14.12.1, 8.4.14.12.2, and 8.4.14.13; ACI 376 (2011 edition) sections 10.7.5 and 10.8.4; U.S. Nuclear Regulatory Commission Regulatory Guide (RG) 1.12 (Revision 3) sections 1 and 3 through 9 and all subsections, or equivalents subject to review and approval. A free-field seismic monitoring device should be included in the seismic monitoring program for the Project site. The proposed seismic monitoring system must include installation location plot plan; description of the triaxial strong motion recorders or other seismic instrumentation; the proposed alarm set points and operating procedures (including emergency operating procedures) for control room operators in response to such alarms/data obtained from seismic instrumentation; and testing and maintenance procedures. | No | Technip | Owner |  | Technip to provide finalized seismic monitoring program for the Project site. | Owner will review, format as necessary and file with FERC in the appropriate Final Design Implementation Plan. |  | Need to discuss. This items probably belong to "Fire and Safety" or other disciplines. This is not Fire & Safety. |  | Permanent Buildings
30 | Prior to construction of final design, Commonwealth shall file with the Secretary the settlement monitoring and maintenance plan that have been reviewed, approved, stamped and sealed by a professional engineer of record registered in the state of Louisiana, which ensures the facilities are protected for the life of the LNG terminal considering settlement, subsidence, and sea level rise. | No | Technip | Owner |  | Technip to provide PE stamped and sealed settlement monitoring and maintenance plan. | Owner will review, format as necessary and file with FERC in the appropriate Final Design Implementation Plan. |  | T.EN prepared and released to bidder the subcontract "Additional Geotechnical Scope of Work", which contains the task 5.1 "Field Settlement Monitoring Program", including settlement maintenance plan. This item addresses the topic of the Actions 27 and 30. This document will be signed and stamped by a Louisiana Professional Engineer. |  | Equipment
31 | Prior to construction of final design, Commonwealth shall file with the Secretary the final design elevation for the structures/buildings outside floodwalls area, including but are not limited to admin office/main control room, maintenance building, elevated flare, marine flare, jetty platform control room, etc. The final design elevation drawings and calculations shall be stamped and sealed by the professional engineer-of-record, registered in the State of Louisiana. | No | Technip | Owner |  | Technip to provide PE stamped and sealed final design elevation for the structures/buildings outside floodwalls area. | Owner will review, format as necessary and file with FERC in the appropriate Final Design Implementation Plan. |  | T.EN will prepare this document to be signed and stamped by a Louisiana Professional Engineer. |  | Marine Facilities / Permanent Buildings / Equipment
Information pertaining to the following specific recommendations shall be filed with the Secretary for review and written approval by the Director of OEP, or the Director’s designee, within the timeframe indicated by each recommendation. Specific engineering, vulnerability, or detailed design information meeting the criteria specified in Order No. 833 (Docket No. RM16-15-000), including security information, shall be submitted as critical energy infrastructure information pursuant to 18 CFR § 388.113. See Critical Electric Infrastructure Security and Amending Critical Energy Infrastructure Information, Order No. 833, 81 Fed. Reg. 93,732 (December 21, 2016), FERC Stats. & Regs. 31,389 (2016). Information pertaining to items such as offsite emergency response, procedures for public notification and evacuation, and construction and operating reporting requirements would be subject to public disclosure. All information shall be filed a minimum of 30 days before approval to proceed is requested.
32 | Prior to initial site preparation, Commonwealth shall file an overall Project schedule, which includes the proposed stages of initial site preparation, construction, commissioning, and in-service plan relative to notice to proceed requests and related conditions. | No | Technip | Owner |  | Technip to provide an overall Project schedule for inclusion in the Site Prepartion IP. | Owner will review, format as necessary and file with FERC in Site Preparation Implementation Plan. |  | Can be filed with package but is subject to change in EPC phase |  | Site Prep. | Schedule part of the contract to be sent to FERC
33 | Prior to initial site preparation, Commonwealth shall file procedures for controlling access during construction. | No | Technip | Owner |  | Technip to provide procedures for access control during construction. | Owner will review, and file with FERC in Site Preparation Implementation Plan. | paperwork filing will be included in HSE/Security plan Permanent Fences Layout = 078051C-0100-DW-1424-0001 Fence Details = 078051C-000-STD-1480-0034-1, 2, 3 | this is with site prep contractor SOW and will be submitted to TEN prior to start | 1006 | Site Prep. | This will be part of HSE/Site Security Plan issued in the LNTP1 phase of the project.
34 | Prior to initial site preparation, Commonwealth shall file quality assurance and quality control procedures for construction activities, including transportation load monitoring for prefabricated process modules and LNG storage tanks. | No | Technip | Owner |  | Technip to provide quality assurance and quality control procedures for construction activities. | Owner will review, format as necessary and file with FERC in Site Preparation Implementation Plan. |  | this is with site prep contractor SOW and will be submitted to TEN prior to start |  | Site Prep. | QA and QC procedures are part of the Site Prep subcon including settlement plate monitoring. However Transportation load monitoring for prefab process modules and LNG storage tanks needs to be clarified with CWLNG FERC rep.
35 | Prior to initial site preparation, Commonwealth shall file with the Secretary the finalized wind design basis for the project facility, which shall include the tornado loads determination and consideration of its load combination as required by ASCE/SEI 7 (2022 edition) or approved equivalent. | No | Technip | Owner |  | Technip to provide finalized wind design basis for the project facility. | Owner will review, format as necessary and file with FERC in Site Preparation Implementation Plan. | Civil/Structural Design Criteria = 078051C-000-JSD-1400-0050 | 03-01-23: The wind design basis, the tornado load determination, and the corresponding load combinations per ASCE 7-22 are included in Section 6.4, 6.15, Chapter 7, and Appendices A, B, and C of the document 078051C-000-JSD-1400-0050-B "Civil / Structural Design Criteria". This action is considered closed. The wind design basis, included in the Civil Structural Design Criteria for the project, will include Tornado Loads per ASCE 7-22. | 1003 | Site Prep. | The wind design basis, the tornado load determination, and the corresponding load combinations per ASCE 7-22 are included in Section 6.4, 6.15, Chapter 7, and Appendices A, B, and C of the document 078051C-000-JSD-1400-0050-B "Civil / Structural Design Criteria". The wind design basis, included in the Civil Structural Design Criteria for the project, will include Tornado Loads per ASCE 7-22. This action is considered closed. Additional queries raised by FERC on Tornado loads were responded by TEN/CWLNG in July, 2024. | Closed
36 | Prior to initial site preparation, Commonwealth shall file its design wind speed criteria for all other facilities not covered by PHMSA’s Letter of Determination to be designed to withstand wind speeds commensurate with the risk and reliability associated with the facilities in accordance with ASCE 7-22 or equivalent. | No | Technip | Owner |  | Technip to provide design wind speed criteria for all facilities not covered by the PHMSA LOD. | Owner will review, format as necessary and file with FERC in Site Preparation Implementation Plan. | Civil/Structural Design Criteria = 078051C-000-JSD-1400-0050 | 03-01-23: The wind speed criteria for the facilities not covered by the Pipeline and Hazardous Materials Safety Administration (PHMSA) will follow the regulations of the ASCE 7-22, and are included in Section 6.4 of the document 078051C-000-JSD-1400-0050-B "Civil / Structural Design Criteria". This action is considered closed. The wind speed criteria, included on the Civil Structural Design Criteria for the project, will consider those facilities not covered by PHMSA's LOD in accordance with ASCE 7-22. | 1004 | Site Prep. | The wind speed criteria for the facilities not covered by the Pipeline and Hazardous Materials Safety Administration (PHMSA) will follow the regulations of the ASCE 7-22, and are included in Section 6.4 of the document 078051C-000-JSD-1400-0050-B "Civil / Structural Design Criteria". This action is considered closed. The wind speed criteria, included on the Civil Structural Design Criteria for the project, considered those facilities not covered by PHMSA's LOD in accordance with ASCE 7-22. | Closed
37 | Prior to initial site preparation, Commonwealth shall develop an Emergency Response Plan (ERP) (including evacuation and any sheltering and re-entry) and coordinate procedures with the U.S. Coast Guard (USCG); state, county, and local emergency planning groups; fire departments; state and local law enforcement; and other appropriate federal agencies. This plan shall be consistent with recommended and good engineering practices and based on potential impacts and onsets of hazards from accidental and intentional events along the LNG marine vessel route and potential impacts and onset of hazards from accidental and intentional events at the LNG terminal, including but not limited to a catastrophic failure of the largest LNG tank. This plan shall address any special considerations and pre-incident planning for infrastructure and public with access and functional needs and shall include at a minimum: a. materials and plans for periodic dissemination of public education and training materials for evacuation and/or shelter in place of the public within any transient hazard areas along the marine vessel route, and within LNG terminal hazard areas; b. plans to competently train emergency responders required to effectively and safely respond to hazardous material incidents including, but not limited to LNG fires and dispersion; c. plans to competently train emergency responders to effectively and safely evacuate or shelter public within transient hazard areas along the marine vessel route, and within hazard areas from LNG terminal; d. designated contacts with federal, state and local emergency response agencies responsible for emergency management and response within any transient hazard areas along the marine vessel route, and within hazard areas from LNG terminal; e. scalable procedures for the prompt notification of appropriate local officials and emergency response agencies based on the level and severity of potential incidents; f. scalable procedures for mobilizing response and establishing a unified command, including identification, location, and design of any emergency operations centers and emergency response equipment required to effectively and safely to respond to hazardous material incidents and evacuate or shelter public within transient hazard areas along the marine vessel route, and within LNG terminal hazard areas; g. scalable procedures for notifying public, including identification, location, design, and use of any permanent sirens or other warning devices required to effectively communicate and warn the public prior to onset of debilitating hazards within any transient hazard areas along the LNG marine vessel route and within hazard areas from LNG terminal; h. scalable procedures for evacuating the public, including identification, location, design, and use of evacuation routes/methods and any mustering locations required effectively and safely evacuate public within any transient hazard areas along the LNG marine transit route and within hazard areas from LNG terminal; and i. scalable procedures for sheltering the public, including identification, location, design, and use of any shelters demonstrated to be needed and demonstrated to effectively and safely shelter public prior to onset of debilitating hazards within transient hazard areas that may better benefit from sheltering in place (i.e., those within Zones of Concern 1 and 2), along the route of the LNG marine vessel and within hazard areas that may benefit from sheltering in place (i.e., those within areas of 1,600 British thermal units (BTU)/ft2 -hr and 10,000 BTU/ft2 -hr radiant heats from fires with farthest impacts, including from a catastrophic failure of largest LNG tank) of the LNG terminal. Commonwealth shall notify the FERC staff of all planning meetings in advance and shall report progress on the development of its ERP at 3‑month intervals. | No | Owner | Technip |  | Technip to provide a finalized Construction, Commissioning and Start-up Emergency Response Plan. Technip will update and provide clarity on plans for emergency response, evacuation, how they will contact officials in an emergency response during construction, commissioning and start-up. | Owner will review and file Construction ERP with FERC in Site Preparation Implementation Plan. Owner will also file Draft version of Operations ERP in Site Preparation Implementation and will notify FERC of all planning meetings in advance and will report progress on the development of its ERP at 3‑month intervals. |  | This will be completed in EPC phase and will not be available. Look in the schedule when this should be issued to CWLNG An ERP for site prep shall be in place for the site prep operation, not the full ERP for the EPC phase of the project |  | Site Prep. | Technip will issue ERP in the LNTP1 phase of the project which will cover construction activities and it will subsequently revised to include commisioning and startup activities in the EPC phase of the project.
38 | Prior to initial site preparation, Commonwealth shall file a Cost-Sharing Plan identifying the mechanisms for funding all Project-specific security/emergency management costs that would be imposed on state and local agencies. This comprehensive plan shall include funding mechanisms for the capital costs associated with any necessary security/emergency management equipment and personnel base. This plan shall include sustained funding of any requirement or resource gap analysis identified to effectively and safely evacuate and shelter public and to effectively and safely respond to hazardous material incidents consistent with recommended and good engineering practices. Commonwealth shall notify FERC staff of all planning meetings in advance and shall report progress on the development of its Cost Sharing Plan at 3-month intervals. | No | Owner | Techip |  | Technip will provide clarity on plans for emergency response and security,hurricane preparedness and how they will contact officials in an emergency response during construction. | Owner to file Cost-Sharing Plan in Site Preparation Implementation Plan. |  |  |  | Site Prep. | Technip will issue ERP in the LNTP1 phase of the project which will cover construction activities and it will subsequently revised to include commisioning and startup activities in the EPC phase of the project. To be discussed with PMT/Construction
39 | Prior to construction of final design of any permanent facilities, Commonwealth shall file Emergency Response Plans and any associated Cost Sharing Plan provisions in coordination with federal, state, and local agencies for hazards that may reach State Highway 27, including identifying potential incidents, impact distances, and timing of the onset of hazards reaching State Highway 27, and measures to notify approaching highway traffic and evacuate persons from impacted areas as quickly as possible relative to the onset of hazards. The ERP and Cost Sharing Plans should discuss consideration of signage or equivalent, and maintenance thereof, to facilitate notification and evacuation. | No | Owner | NA |  | None | Owner to file with FERC Cost-Sharing Plan and Emergency Response Plans for hazards that may reach State highway 27 during operations in Site Preparation Implementation Plan. |  |  |  | Site Prep. | Technip will issue ERP in the LNTP1 phase of the project which will cover construction activities and it will subsequently revised to include commisioning and startup activities in the EPC phase of the project. To be discussed with PMT/Construction DOT study report can also be included as part of the package for this point.
40 | Prior to construction of final design, Commonwealth shall file change logs that list and explain any changes made from the front-end-engineering-design (FEED) provided in Commonwealth’s application and filings. A list of all changes with an explanation for the design alteration shall be provided and all changes shall be clearly indicated on all diagrams and drawings. | No | Technip | Owner |  | Technip to provide change logs with associated diagrams and drawings which clearly indicate changes from FEED to final design. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). |  |  |  | U/G Piping / A/G Piping
41 | Prior to construction of final design, Commonwealth shall file information/revisions pertaining to Commonwealth’s response: numbers 15, 45, 65, and 106 of its February 4, 2020 filing; numbers 124, 125c, 127, 134, 135, 148, 153, 154, 155, 157, 161, 162, 164, 165, and 167 of its March 4, 2020 filing; numbers 7, 17, and 18 of its June 4, 2021 filing; numbers 5, 23, 27, 28, 29, 30, 31, 32, and 33 of its November 9, 2021 filing, which indicated features to be included or considered in the final design. | No | Technip | Owner |  | Technip to provide information/revisions pertaining to all data request responses listed in the Condition. Information/revisions should be provided prior to construction of final design for each of the various elements of the Project addressed in the data request responses. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). Owner will provide guidance on which responses should be included in the various IP filings for the separate work activities. |  |  |  | A/G Piping
42 | Prior to construction of final design, Commonwealth shall file drawings and specifications for crash rated vehicle barriers in accordance with American Society for Testing and Materials (ASTM) F2656 (2015 edition) or approved equivalent at each facility entrance for access control. The crash rating vehicle type shall be supported by a security vulnerability assessment that takes into account the potential target attractiveness, threats, vulnerabilities, consequences, and mitigation effectiveness consistent with American Institute of Chemical Engineers, Guidelines for Analyzing and Managing the Security Vulnerabilities of Fixed Chemical Sites, 2003 or approved equivalent. The crash rating speed shall be supported by an analysis of the maximum attainable vehicle velocity based on vehicle type acceleration and road characteristics (e.g., straight length, radius of curvature, sloped/banked, coefficient of friction, etc.). | No | Technip | Owner |  | Technip to provide drawings and specifications for crash rated vehicle barriers at each facility entrance for access control. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. | This is a transportation vehicle topic that require specialized external assistance. |  |  | Security/ Lighting/ Intrusion Detection
43 | Prior to construction of final design, Commonwealth shall file drawings of internal road vehicle protections, such as guard rails, barriers, and bollards to protect transfer piping, pumps, compressors, hydrants, monitors, etc. to ensure that they are located away from roadway or protected from inadvertent damage from vehicles. | Yes | Technip | Owner |  | Technip to provide drawings of internal road vehicle protections. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. |  | The final grade drawing, part of the Site Preparation Package, will contains details about internal roads, vehicle protection (guardrails, barriers and bollards) to protect transfer piping, pumps, compressors, hydrants, monitors, etc. against potential damages from vehicles. |  | Security/ Lighting/ Intrusion Detection
44 | Prior to construction of final design, Commonwealth shall file drawings of the security fence. The fencing drawings shall provide details of fencing that demonstrates it is in accordance with NFPA 59A (2019 edition) or approved equivalent and would restrict and deter access around the entire facility and has a setback from exterior features (e.g., power lines, trees, etc.) and from interior features (e.g., piping, equipment, buildings, etc.) that does not allow the fence to be overcome. | No | Technip | Owner |  | Technip to provide drawings of the security fence that are in accordance with NFPA 59A (2019 edition) or approved equivalent. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. |  | 03-01-23: The security fence and all its design details that meet the NFPA 59A code, 2019 edition, are shown in drawings 078051C-000-STD-1480-0034-1, 078051C-000-STD-1480-0034-2 and 078051C-000-STD-1480-0034-3. On the other hand, the location of the security fence is indicated in drawings 078051C-0100-DW-1421-0001-1, 078051C-0100-DW-1423-0003, and 078051C-0100-DW-1424-0001. These drawings show deter access around the facility and setbacks from exterior features like power lines, tress, etc.; and from interior features like piping, equipments, wells, buildings, etc. The fence's design intention is to do not allow transpassing. The security fence, which is part of the Site Preparation Package as it was explained in detail on item # 22, will contains all design and details compliying NFPA 59A (2019 Edition), indicating deter access around the facility and setbacks from exterior features like power lines, tress, etc., and from interior features like piping, equipments, wells, buildings. The fence design intention is to do not allow transpassing. | 1005 | Security/ Lighting/ Intrusion Detection
45 | Prior to construction of final design, Commonwealth shall file security camera and intrusion detection drawings. The security camera drawings shall show the locations, mounting elevation, areas covered, and features of each camera (e.g., fixed, tilt/pan/zoom, motion detection alerts, low light, etc.) and shall provide camera coverage at access points and along the entire perimeter with redundancies and camera coverage interior of the facility to enable rapid monitoring of the terminal, including a camera at the top of each LNG storage tank, and coverage within pretreatment areas, within liquefaction areas, within truck transfer areas, within marine transfer areas, and within buildings. The drawings shall show or note the location and type of the intrusion detection and shall cover the entire perimeter of the facility. | No | Technip | Owner |  | Technip to provide security camera and intrusion detection drawings. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. |  |  |  | Security/ Lighting/ Intrusion Detection
46 | Prior to construction of final design, Commonwealth shall file photometric analyses or equivalent and associated lighting drawings. The lighting drawings shall show the location, elevation, type of light fixture, and lux levels of the lighting system and shall provide illumination along the perimeter of the terminal, process equipment, mooring points, and along paths/roads of access and egress to facilitate security monitoring and emergency response operations in accordance with API 540 (4th edition) or approved equivalent and applicable federal regulations. | No | Technip | Owner |  | Technip to provide photometric analyses or equivalent and associated lighting drawings. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. |  |  |  | Security/ Lighting/ Intrusion Detection
47 | Prior to construction of final design, Commonwealth shall file a plot plan of the final design showing all major equipment, structures, buildings, and impoundment systems. | No | Technip | Owner |  | Technip to provide plot plan of the final design. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. |  | Plot plans are always being updated |  | Equipment
48 | Prior to construction of final design, Commonwealth shall file a building siting assessment to ensure plant buildings that are occupied or critical to the safety of the LNG plant are adequately protected from potential hazards involving fires and vapor cloud explosions. | No | Technip | Owner |  | Technip to provide building site assessment. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. |  | Facility Siting Study completed and design accidental loads provided for occupied and critical buildings. Facility Siting Study 078051C-000-RT-1990-0003_B Building Matrix 078051C-000-NM-2000-0001 |  | Permanent Buildings
49 | Prior to construction of final design, Commonwealth shall file threedimensional plant drawings to confirm plant layout for maintenance, access, egress, and congestion. | No | Technip | Owner |  | Technip to provide three dimensional plant drawings. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. |  |  |  | A/G Piping / LNG Tanks / Permanent Buildings / Equipment
50 | Prior to construction of final design, Commonwealth shall file up-to-date process flow diagrams (PFDs), heat and mass balances (HMBs), and piping and instrument diagrams (P&IDs), including vendor P&IDs. The HMBs shall demonstrate a peak export rate of 9.5 million metric tonnes per annum. The P&IDs shall include the following information: a. equipment tag number, name, size, duty, capacity, and design conditions; b. equipment insulation type and thickness; c. storage tank pipe penetration size and nozzle schedule; d. valve high pressure side and internal and external vent locations; e. piping with line number, piping class specification, size, and insulation type and thickness; f. piping specification breaks and insulation limits; g. all control and manual valves numbered; h. relief valves with size and set points; and i. drawing revision number and date. | No | Technip | Owner |  | Technip to provide PFDs, HMBs and P&IDs with HMBs export rate of 9.5 mtpa. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. |  |  |  | U/G Piping / A/G Piping / LNG Tanks / Equipment
51 | Prior to construction of final design, Commonwealth shall file P&IDs, specifications, and procedures that clearly show and specify the tie-in details required to safely connect subsequently constructed facilities with the operational facilities. | No | Technip | Owner |  | Technip to provide P&IDs, specifications, and procedures that clearly show and specify the tie-in details. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. |  |  |  | A/G Piping
52 | Prior to construction of final design, Commonwealth shall file a car seal and lock philosophy and car seal and lock program, including a list of all car-sealed and locked valves consistent with the P&IDs. The car seal and lock program should include monitoring and periodically reviewing correct car seal and lock placement and valve position. | No | Technip | Owner |  | Technip to provide car seal and lock philosophy and car seal and lock program, including a list of all car-sealed and locked valves consistent with the P&IDs. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. |  |  |  | A/G Piping
53 | Prior to construction of final design, Commonwealth shall file information to demonstrate the Engineering Procurement and Construction (EPC) contractor has verified that all FEED hazard identification recommendations have been addressed. | No | Technip | Owner |  | Technip to provide information and verification that all FEED hazard identification recommendations have been addressed. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. | Provide a closeout process for HAZID and HAZOP recommendations and Implement it. (Bill) |  |  | A/G Piping
54 | Prior to construction of final design, Commonwealth shall file a hazard and operability review of the final design P&IDs, a list of the resulting recommendations, and action taken on the recommendations. The issued for construction P&IDs shall incorporate the hazard and operability review recommendations and justification shall be provided for any recommendations that are not implemented. | No | Technip | Owner |  | Technip to provide hazard and operability review of the final design P&IDs, a list of the resulting recommendations, and action taken on the recommendations | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. |  | This is for next phase after DED HAZOP |  | A/G Piping
55 | Prior to construction of final design, Commonwealth shall file design pressure and set point information for the piping, equipment, and pressure relief valves located between the inlet feed gas high integrity pressure protection system (HIPPS) and the downstream pressure regulators to demonstrate pressures would not exceed the design pressures of these components. | No | Technip | Owner |  | Technip to provide design pressure and set point information for the piping, equipment, and pressure relief valves located between the inlet feed gas high integrity pressure protection system (HIPPS) and the downstream pressure regulators to demonstrate pressures would not exceed the design pressures of these components. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. |  |  |  | A/G Piping
56 | Prior to construction of final design, Commonwealth shall provide a check valve upstream of the acid gas removal column to prevent backflow or provide a dynamic simulation that shows that upon plant shutdown, the swan neck would be sufficient for this purpose. | Yes | Technip | Owner |  | Technip to provide provide a check valve upstream of the acid gas removal column to prevent backflow or provide a dynamic simulation that shows that upon plant shutdown, the swan neck would be sufficient for this purpose. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan a dynamic simulation if Technip does not provide check valve. |  |  |  | A/G Piping
57 | Prior to construction of final design, Commonwealth shall specify a second source of vacuum breaker gas (i.e., pad gas) for the LNG storage tanks independent of the liquefaction facility. | Yes | Technip | Owner |  | Technip to specify in final design a second source of vacuum breaker gas (i.e., pad gas) for the LNG storage tanks independent of the liquefaction facility. | Owner to reference Condition in appropriate Final Design Implementation Plan and reference P&ID (or other document) in which compliance is demonstrated. |  |  |  | LNG Tanks
58 | Prior to construction of final design, Commonwealth shall include LNG tank fill flow measurement with high flow alarm. | Yes | Technip | Owner |  | Technip to include in final design LNG tank fill flow measurement with high flow alarm. | Owner to reference Condition in appropiate Final Design Implementation Plan and reference P&IDs (or other document) in which compliance is demonstrated. |  |  |  | LNG Tanks
59 | Prior to construction of final design, Commonwealth shall specify a discretionary vent valve on each LNG storage tank that is operable through the Distributed Control System (DCS). In addition, a car sealed open manual block valve shall be provided upstream of the discretionary vent valve. | Yes | Technip | Owner |  | Technip to specify in final design a discretionary vent valve on each LNG storage tank that is operable through the Distributed Control System (DCS). In addition, a car sealed open manual block valve shall be provided upstream of the discretionary vent valve. | Owner to reference Condition in appropiate Final Design Implementation Plan and reference P&IDs (or other document) in which compliance is demonstrated. |  | P&ID 078051C-030-PID-0031-0013 was updated to show the vent valves on all tanks and will be sent to the Subcontractors for their design. | 1007 | LNG Tanks
60 | Prior to construction of final design, Commonwealth shall file the safe operating limits (upper and lower), alarm and shutdown set points for all instrumentation (e.g., temperature, pressures, flows, and compositions). | Yes | Technip | Owner |  | Technip to provide the safe operating limits (upper and lower), alarm and shutdown set points for all instrumentation (e.g., temperature, pressures, flows, and compositions). | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. |  |  |  | Elec./ Instr.
61 | Prior to construction of final design, Commonwealth shall file cause-and-effect matrices for the process instrumentation, fire and gas detection system, and emergency shutdown system. The cause-and-effect matrices shall include alarms and shutdown functions, details of the voting and shutdown logic, and set points. | No | Technip | Owner |  | Technip to provide cause-and-effect matrices for the process instrumentation, fire and gas detection system, and emergency shutdown system. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan. |  |  |  | Hazard Detection/ Hazard Control/ Fire Protection/ESD
62 | Prior to construction of final design, Commonwealth shall specify that all emergency shutdown valves are to be equipped with open and closed position switches connected to the Distributed Control System (DCS)/ safety instrument system (SIS). | Yes | Technip | Owner |  | Technip to specify in final design that all emergency shutdown valves are to be equipped with open and closed position switches connected to the Distributed Control System (DCS)/ safety instrument system (SIS). | Owner to reference Condition in appropiate Final Design Implementation Plan and reference documents in which compliance is demonstrated. |  |  |  | Hazard Detection/ Hazard Control/ Fire Protection/ESD
63 | Prior to construction of final design, Commonwealth shall demonstrate that all electrical, instrument, and control systems at the project, which activate emergency systems or are relied upon for isolation or shutdowns, will be designed to withstand a 20-minute fire exposure per UL 1709 (6th edition) or approved equivalent. | No | Technip | Owner |  | Technip to demonstrate in final design that all electrical, instrument, and control systems at the project, which activate emergency systems or are relied upon for isolation or shutdowns, will be designed to withstand a 20-minute fire exposure per UL 1709 (6th edition) or approved equivalent. | Owner to reference Condition in appropiate Final Design Implementation Plan and reference documents in which compliance is demonstrated. |  |  |  | Hazard Detection/ Hazard Control/ Fire Protection/ESD
64 | Prior to construction of final design, Commonwealth shall file an up-to-date equipment list, process and mechanical data sheets, and specifications. The specifications shall include: a. building specifications (e.g., control buildings, electrical buildings, compressor buildings, storage buildings, pressurized buildings, ventilated buildings, blast resistant buildings); b. mechanical specifications (e.g., piping, valve, insulation, rotating equipment, heat exchanger, storage tank and vessel, other specialized equipment); c. electrical and instrumentation specifications (e.g., power system, control system, SIS, cable, other electrical and instrumentation); and d. security and fire safety specifications (e.g., security, passive protection, hazard detection, hazard control, firewater). | No | Technip | Owner |  | Technip to provide an up-to-date equipment list, process and mechanical data sheets, and specifications. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). |  |  |  | Marine Facilities / U/G Piping / A/G Piping / LNG Tanks / Permanent Buildings / Equipment Hazard Detection/ Hazard Control/ Fire Protection/ESD / Elec./ Instr. / Security/ Lighting/ Intrusion Detection
65 | Prior to construction of final design, Commonwealth shall file a list of all codes and standards and the final specification document number where they are referenced. | No | Technip | Owner |  | Technip to provide a list of all codes and standards and the final specification document number where they are referenced. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s).
66 | Prior to construction of final design, Commonwealth shall file a complete specifications and drawings of the proposed LNG tank design and installation. | No | Technip | Owner |  | Technip to provide a complete specifications and drawings of the proposed LNG tank design and installation. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). |  |  |  | LNG Tanks
67 | Prior to construction of final design, Commonwealth shall file an evaluation of emergency shutdown valve closure times. The evaluation shall account for the time to detect an upset or hazardous condition, notify plant personnel, and close the emergency shutdown valve(s). | No | Technip | Owner |  | Technip to provide an evaluation of emergency shutdown valve closure times. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | This will be part of the Safety Requirement Specification for all Safety Instrument Functions. To be completed in DED. |  |  | Hazard Detection/ Hazard Control/ Fire Protection/ESD
68 | Prior to construction of final design, Commonwealth shall file an evaluation of dynamic pressure surge effects from valve opening and closure times and pump operations that demonstrate that the surge effects do not exceed the design pressures. | No | Technip | Owner |  | Technip to provide an evaluation of dynamic pressure surge effects from valve opening and closure times and pump operations that demonstrate that the surge effects do not exceed the design pressures. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s).
69 | Prior to construction of final design, Commonwealth shall demonstrate that, for hazardous fluids, piping and piping nipples 2 inches or less in diameter are designed to withstand external loads, including vibrational loads in the vicinity of rotating equipment and operator live loads in areas accessible by operators. | No | Technip | Owner |  | Technip to demonstrate that, for hazardous fluids, piping and piping nipples 2 inches or less in diameter are designed to withstand external loads, including vibrational loads in the vicinity of rotating equipment and operator live loads in areas accessible by operators. | Owner to reference Condition in appropiate Final Design Implementation Plan and reference documents in which compliance is demonstrated.
70 | Prior to construction of final design, Commonwealth shall clearly specify the responsibilities of the LNG tank contractor and the EPC contractor for the piping associated with the LNG storage tank. | No | Technip | Owner |  | Technip to clearly specify the responsibilities of the LNG tank contractor and the EPC contractor for the piping associated with the LNG storage tank. | Owner to reference Condition in appropiate Final Design Implementation Plan and reference documents in which compliance is demonstrated. |  |  |  | LNG Tanks
71 | Prior to construction of final design, Commonwealth shall file the sizing basis and capacity for the final design of the flares and/or vent stacks as well as the pressure and vacuum relief valves for major process equipment, vessels, and storage tanks. | No | Technip | Owner |  | Technip to provide the sizing basis and capacity for the final design of the flares and/or vent stacks as well as the pressure and vacuum relief valves for major process equipment, vessels, and storage tanks. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). |  |  |  | LNG Tanks / Equipment
72 | Prior to construction of final design, Commonwealth shall file the sizing calculations for the PSVs of the following vessels: E-A0101 Inlet Gas Preheater, E-A0403 Demethanizer Reboiler, E-A0301 Regeneration gas hot oil heater. Specifically, the calculations shall show the influence of the backpressure on these PSVs since they vent to the hot oil expansion drum (V-2101A) instead of the flare. | No | Technip | Owner |  | Technip to provide the sizing calculations for the PSVs of the following vessels: E-A0101 Inlet Gas Preheater, E-A0403 Demethanizer Reboiler, E-A0301 Regeneration gas hot oil heater. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). |  |  |  | Equipment
73 | Prior to construction of final design, Commonwealth shall specify the process vessels, and storage vessels for ethylene, propane, isopentane, condensate, hot oil, and LNG are installed with spare pressure relief valves to ensure overpressure protection during relief valve testing or maintenance. | Yes | Technip | Owner |  | Technip to specify in final design the process vessels, and storage vessels for ethylene, propane, isopentane, condensate, hot oil, and LNG are installed with spare pressure relief valves to ensure overpressure protection during relief valve testing or maintenance. | Owner to reference Condition in appropiate Final Design Implementation Plan and reference documents in which compliance is demonstrated. |  |  |  | Equipment
74 | Prior to construction of final design, Commonwealth shall file an updated fire protection evaluation of the proposed facilities. A copy of the evaluation, a list of recommendations and supporting justifications, and actions taken on the recommendations shall be filed. The evaluation shall justify the type, quantity, and location of hazard detection and hazard control, passive fire protection, emergency shutdown and depressurizing systems, firewater, and emergency response equipment, training, and qualifications in accordance with NFPA 59A (2001). The justification for the flammable and combustible gas detection and flame and heat detection systems shall be in accordance with International Society of Automation (ISA) 84.00.07 (2018 edition) or approved equivalent methodologies and would need to demonstrate 90 % or more of releases (unignited and ignited) that could result in an off-site or cascading impact would be detected by two or more detectors and result in isolation and de inventory within 10 minutes. The analysis shall take into account the set points, voting logic, wind speeds, and wind directions. The justification for firewater shall provide calculations for all firewater demands based on design densities, surface area, and throw distance as well as specifications for the corresponding hydrant and monitors needed to reach and cool equipment. | No | Technip | Owner |  | Technip to provide an updated fire protection evaluation of the proposed facilities. A copy of the evaluation, a list of recommendations and supporting justifications, and actions taken on the recommendations to be provided by Technip. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | 1. Update NFPA 59A Preliminary Fire Protection Evaluation - this is not a current deliverable (T.EN - Edgar). This report is not originated by T.EN, therefore shall be updated by CWLNG. Add it to the deliverable list and define issuing date. This can't be added in the deliverable list since T.EN will not update this document (T.EN-Edgar) 2. Provide vendor list for Fire & Gas Mapping Study to be conducted in this phase., (T.EN - Edgar) Sent email to CWLNG (Chandra) for the list of potential consultants. T.EN Vendor list currently does not have vendor for this service. Potentially need more than two vendors. Invite couple of potential vendors to learn if their servive meets FEIS expectations. (Edgar) Noted in F&S Spec Rev 4 |  |  | Hazard Detection/ Hazard Control/ Fire Protection/ESD
75 | Prior to construction of final design, Commonwealth shall file spill containment system drawings with dimensions and slopes of curbing, trenches, impoundments, tertiary containment and capacity calculations considering any foundations and equipment within impoundments, as well as the sizing and design of the downcomers. The spill containment drawings shall show containment for all hazardous fluids including all liquids handled above their flashpoint, from the largest flow from a single line for 10 minutes, including de-inventory, or the maximum liquid from the largest vessel (or total of impounded vessels) or otherwise demonstrate that providing spill containment would not significantly reduce the flammable vapor dispersion or radiant heat consequences of a spill. | No | Technip | Owner |  | Technip to provide spill containment system drawings with dimensions and slopes of curbing, trenches, impoundments, tertiary containment and capacity calculations considering any foundations and equipment within impoundments, as well as the sizing and design of the downcomers. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). |  | This action is shared between Civil and "Fire & Safety" or "Process Safety" or "HSE" Departments. Civil will provide slopes, trenches, curbing and impoundments. The topics related to tertoary containments and capacity calculations is by other parties inside T.EN. The spill containment drawings is by Process Safety. |  | Spill Cont. Systems
76 | Prior to construction of final design, Commonwealth shall file an analysis that demonstrates the flammable vapor dispersion from design spills would be prevented from dispersing underneath the elevated LNG storage tanks, or the LNG storage tanks would be able to withstand an overpressure due to ignition of the flammable vapor that disperses underneath the elevated LNG storage tanks. | No | Technip | Owner |  | Technip to provide an analysis that demonstrates the flammable vapor dispersion from design spills would be prevented from dispersing underneath the elevated LNG storage tanks, or the LNG storage tanks would be able to withstand an overpressure due to ignition of the flammable vapor that disperses underneath the elevated LNG storage tanks. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Requires CFD analysis, will need a 3rd party to conduct. |  |  | LNG Tanks
77 | Prior to construction of final design, Commonwealth shall file an analysis that demonstrates the flammable vapor dispersion from design spills would be prevented from dispersing underneath the elevated control room, or the control room would be able to withstand an overpressure due to ignition of the flammable vapor that disperses underneath the elevated control room. | No | Technip | Owner |  | Technip to provide an analysis that demonstrates the flammable vapor dispersion from design spills would be prevented from dispersing underneath the elevated control room, or the control room would be able to withstand an overpressure due to ignition of the flammable vapor that disperses underneath the elevated control room. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Requires CFD analysis, will need a 3rd party to conduct. |  |  | Permanent Buildings
78 | Prior to construction of final design, Commonwealth shall file a technical review of its proposed facility design that evaluates other potential locations for the proposed control room, or additional mitigation measures to protection the control room from high radiant heats. | No | Technip | Owner |  | Technip to provide a technical review of its proposed facility design that evaluates other potential locations for the proposed control room, or additional mitigation measures to protection the control room from high radiant heats. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Facility Siting Study will address. Do a sensitivity study for alternate locations for the control room. | Facility Siting Study completed and provides design accidental loads for the current Administration and Control Building. Design accidental loads were also determined for alternate location of a standalone control room in a lower risk location on the site. Facility Siting Study 078051C-000-RT-1990-0003_B Building Matrix 078051C-000-NM-2000-0001 |  | Permanent Buildings
79 | Prior to construction of final design, Commonwealth shall file electrical area classification drawings, including cross sectional drawings. The drawings shall demonstrate compliance with NFPA 59A (2019 edition), NFPA 70 (2017 edition), NFPA 497 (2017 edition), and API RP 500 (3rd edition), or approved equivalents. In addition, the drawings shall include revisions to the electrical area classification design or provide technical justification that supports the electrical area classification of the following areas using most applicable API RP 500 figures (e.g., figures 20 and 21) or hazard modeling of various release rates from equivalent hole sizes and wind speeds (see NFPA 497 release rate of 1 lbmole/minute). | No | Technip | Owner |  | Technip to provide file electrical area classification drawings, including cross sectional drawings. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | IFR currently, will be completed in EPC |  |  | Elec./ Instr.
80 | Prior to construction of final design, Commonwealth shall file analysis of the buildings containing hazardous fluids and the ventilation calculations that limit concentrations below the lower flammable limits (LFL) (e.g., 25-percent LFL), including an analysis of off gassing of hydrogen in battery rooms, and shall also provide hydrogen detectors that alarm (e.g., 20- to 25-percent LFL) and initiate mitigative actions (e.g., 40- to 50-percent LFL) in accordance with NFPA 59A (2019 edition) and NFPA 70 (2017 edition), or approved equivalents. | No | Technip | Owner |  | Technip to provide analysis of the buildings containing hazardous fluids and the ventilation calculations. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Discuss with CSA (Lab) and Electrical (Battery room) Ensure Ventilation System specification incorporates the analysis. Identify specifications impacted and timing. Noted in F&S Spec - Rev. D | This action needs to be reclassified to "Fire & Safety" or "Process Safety" or "HSE" Departments. |  | Permanent Buildings
81 | Prior to construction of final design, Commonwealth shall file drawings and details of how process seals or isolations installed at the interface between a flammable fluid system and an electrical conduit or wiring system meet the requirements of NFPA 59A (2001) or approved equivalent. | No | Technip | Owner |  | Technip to provide drawings and details of how process seals or isolations installed at the interface between a flammable fluid system and an electrical conduit or wiring system meet the requirements of NFPA 59A (2001) or approved equivalent. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). |  |  |  | Elec./ Instr.
82 | Prior to construction of final design, Commonwealth shall file details of an air gap or vent installed downstream of process seals or isolations installed at the interface between a flammable fluid system and an electrical conduit or wiring system. Each air gap shall vent to a safe location and be equipped with a leak detection device that shall continuously monitor for the presence of a flammable fluid, alarm the hazardous condition, and shut down the appropriate systems. | No | Technip | Owner |  | Technip to provide details of an air gap or vent installed downstream of process seals or isolations installed at the interface between a flammable fluid system and an electrical conduit or wiring system. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). |  |  |  | Elec./ Instr.
83 | Prior to construction of final design, Commonwealth shall file complete drawings and a list of the hazard detection equipment. The drawings shall clearly show the location and elevation of all detection equipment as well as their coverage area. The list shall include the instrument tag number, type and location, alarm indication locations, and shutdown functions of the hazard detection equipment. | No | Technip | Owner |  | Technip to provide complete drawings and a list of the hazard detection equipment. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Fire & Gas Layout Drawings include this information. | Fire and Gas System Layout Drawings, tabulation of devices and Cause & Effect Diagrams will be issued in this Phase. (T.EN - Edgar) Specify planned issue dates. (Edgar) |  | Hazard Detection/ Hazard Control/ Fire Protection/ESD
84 | Prior to construction of final design, Commonwealth shall file a technical review of facility design that: a. identifies all combustion/ventilation air intake equipment and the distances to any possible flammable gas or toxic release; and b. demonstrates that these areas are adequately covered by hazard detection devices and indicates how these devices would isolate or shutdown any combustion or heating ventilation and air conditioning equipment whose continued operation could add to or sustain an emergency. | No | Technip | Owner |  | Technip to provide a technical review of facility design pertaining to items a and b. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Fire & Gas Layout Drawings include this information, with the exception of distances to leak sources. | Fire and Gas System Layout Drawings will be issued in this Phase. (T.EN - Edgar) This requirement is seeking additional information? Would this be a separate document? (Edgar) |  | Hazard Detection/ Hazard Control/ Fire Protection/ESD
85 | Prior to construction of final design, Commonwealth shall file a design that includes hazard detection suitable to detect high temperatures and smoldering combustion products in electrical buildings and control room buildings. | No | Technip | Owner |  | Technip to provide a design that includes hazard detection suitable to detect high temperatures and smoldering combustion products in electrical buildings and control room buildings. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Fire & Gas Building Specification | Fire and Safety Specification for Buildings will be issued in this Phase. (T.EN - Edgar) What about the Fire & Gas layout for buildings? (Edgar) Fire & Gas Layout will be done by the building contractor(s). |  | Hazard Detection/ Hazard Control/ Fire Protection/ESD
86 | Prior to construction of final design, Commonwealth shall file an evaluation of the voting logic and voting degradation for hazard detectors. | No | Technip | Owner |  | Technip to provide an evaluation of the voting logic and voting degradation for hazard detectors. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Fire and Gas Cause & Effect Diagram addresses the voting logic. Fire and Safety Philosophy addresses the voting degradation. Noted in F&S Spec - Rev 4 |  |  | Hazard Detection/ Hazard Control/ Fire Protection/ESD
87 | Prior to construction of final design, Commonwealth shall file a list of alarm and shutdown set points for all hazard detectors that account for the calibration gas of the hazard detectors when determining the lower flammable limit set points for methane, ethylene, propane, isopentane, and condensate. | No | Technip | Owner |  | Technip to provide a list of alarm and shutdown set points for all hazard detectors that account for the calibration gas of the hazard detectors when determining the lower flammable limit set points for methane, ethylene, propane, isopentane, and condensate. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Fire and Gas Cause & Effect Diagram addresses the setpoints. | Fire and Gas Cause and Effect will be issued in this Phase. (T.EN - Edgar) What about setpoints for methane, ethylene, propane, iso-pentane and condensate. Discuss with gas detector vendors about this issue as well as the problems with gas detectors in Freeport. (Edgar) |  | Hazard Detection/ Hazard Control/ Fire Protection/ESD
88 | Prior to construction of final design, Commonwealth shall file a list of alarm and shutdown set points for all hazard detectors that account for the calibration gas of hazard detectors when determining the set points for toxic components such as condensate and hydrogen sulfide. | No | Technip | Owner |  | Technip to provide a list of alarm and shutdown set points for all hazard detectors that account for the calibration gas of hazard detectors when determining the set points for toxic components such as condensate and hydrogen sulfide. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Fire and Gas Cause & Effect Diagram addresses the setpoints. | Fire and Gas Cause and Effect will be issued in this Phase. (T.EN - Edgar) |  | Hazard Detection/ Hazard Control/ Fire Protection/ESD
89 | Prior to construction of final design, Commonwealth shall file a drawing showing the location of the emergency shutdown buttons, including, but not limited to the refrigerant storage, condensate storage, and LNG storage areas. Emergency shutdown buttons shall be easily accessible, conspicuously labeled, and located in an area which would be accessible during an emergency. | No | Technip | Owner |  | Technip to provide a drawing showing the location of the emergency shutdown buttons. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | ESD Pushbutton Location Plan | ESD Push Button Location Plan will be issued in this Phase. (T.EN - Edgar) |  | Hazard Detection/ Hazard Control/ Fire Protection/ESD
90 | Prior to construction of final design, Commonwealth shall file facility plan drawings and a list of the fixed and wheeled dry-chemical, hand-held fire extinguishers, and other hazard control equipment. Plan drawings shall clearly show the location by tag number of all fixed, wheeled, and hand-held extinguishers and shall demonstrate the spacing of extinguishers meet prescribed NFPA 10 (2018 edition) or approved equivalent travel distances. The list shall include the equipment tag number, type, capacity, equipment covered, discharge rate, and automatic and manual remote signals initiating discharge of the units and shall demonstrate they meet NFPA 59A (2019 edition) or approved equivalent. | No | Technip | Owner |  | Technip to provide facility plan drawings and a list of the fixed and wheeled dry-chemical, hand-held fire extinguishers, and other hazard control equipment. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Fire and Safety Equipment Layout | Fire & Safety Equipment Drawings which consists of portable fire extinguishers, fixed dry chemical systems, and safety shower combination unit will be issued this Phase. (T.EN - Edgar) |  | Hazard Detection/ Hazard Control/ Fire Protection/ESD
91 | Prior to construction of final design, Commonwealth shall file drawings and specifications for the structural passive protection systems to protect equipment and supports from cryogenic releases. | No | Technip | Owner |  | Technip to provide drawings and specifications for the structural passive protection systems to protect equipment and supports from cryogenic releases. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Fire Exposed Envelope Drawings, with an added legend to show cryogenic protection. Cryogenic spill protection philosophy and preliminary assessment will address location and extent. May need separate drawings to show envelopes in 3D or at least different module levels. Remove preliminary from report. In philosophy, define whether or not spill protection is required for areas containing only welded pipe. Also, confirm when thickness is defined. | FEE Maps will be issued this Phase that will show both passive fire protection and cryogenic coverages for structures. (T.EN - Edgar) May need separate drawings. |  | Hazard Detection/ Hazard Control/ Fire Protection/ESD
92 | Prior to construction of final design, Commonwealth shall file calculations or test results for the structural passive protection systems to protect equipment and supports from cryogenic releases. | No | Technip | Owner |  | Technip to provide calculations or test results for the structural passive protection systems to protect equipment and supports from cryogenic releases. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). |  | Documentations from cryogenic protection vendor are required to close this action item. (T.EN - F&S and Mechanical) Vendor identification in this phase for suitability and cost. |  | Hazard Detection/ Hazard Control/ Fire Protection/ESD
93 | Prior to construction of final design, Commonwealth shall file drawings and specifications for the structural passive protection systems to protect equipment and supports from pool and jet fires. | No | Technip | Owner |  | Technip to provide drawings and specifications for the structural passive protection systems to protect equipment and supports from pool and jet fires. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | This would be vendor data from the purchased product. Not clear who have this responsibility (seems like CSA) | Documentations from PFP protection vendor are required to close this action item. (T.EN - F&S and Mechanical) Vendor identification in this phase for suitability and cost. |  | Hazard Detection/ Hazard Control/ Fire Protection/ESD
94 | Prior to construction of final design, Commonwealth shall file a detailed quantitative analysis to demonstrate that adequate mitigation would be provided for each pressure vessel that could fail within the 4,000 BTU/ft2-hr zone from a pool or jet fires; each critical structural component (including the LNG marine vessel) and emergency equipment item that could fail within the 4,900 BTU/ft2-hr zone from a pool or jet fire; and each occupied building that could expose unprotected personnel within the 1,600 BTU/ft2-hr zone from a pool or jet fire. Trucks at truck transfer stations shall be included in the analysis of potential pressure vessel failures, as well as measures needed to prevent cascading impact due to the 10-minute sizing spill at the marine area. A combination of passive and active protection for pool fires and passive and/or active protection for jet fires shall be provided and demonstrate the effectiveness and reliability. Effectiveness of passive mitigation shall be supported by calculations or test results for the thickness limiting temperature rise over the fire duration, and active mitigation shall be supported by reliability information by calculations or test results, such as demonstrating flow rates and durations of any cooling water would mitigate the heat absorbed by the component. The total firewater demand shall account for all components that could fail to a pool or jet fire. | No | Technip | Owner |  | Technip to provide a detailed quantitative analysis to demonstrate that adequate mitigation for each pressure vessel that could fail within the 4,000 BTU/ft2-hr zone from a pool or jet fires; each critical structural component (including the LNG marine vessel) and emergency equipment item that could fail within the 4,900 BTU/ft2-hr zone from a pool or jet fire; and each occupied building that could expose unprotected personnel within the 1,600 BTU/ft2-hr zone from a pool or jet fire. Trucks at truck transfer stations shall be included in the analysis of potential pressure vessel failures, as well as measures needed to prevent cascading impact due to the 10-minute sizing spill at the marine area. A combination of passive and active protection for pool fires and passive and/or active protection for jet fires shall be provided and demonstrate the effectiveness and reliability. Effectiveness of passive mitigation shall be supported by calculations or test results for the thickness limiting temperature rise over the fire duration, and active mitigation shall be supported by reliability information by calculations or test results, such as demonstrating flow rates and durations of any cooling water would mitigate the heat absorbed by the component. The total firewater demand shall account for all components that could fail to a pool or jet fire. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Facility Siting Study will identify thermal radiation contours and any mitigation needed for occupied or critical buildings. Mitigation for other equipment is not in current scope. | Thermal radiation contours have been developed in the Facility Siting Study, and form the basis for location of PFP in locations beyond that required by API 2218. Fire & Safety is responsible for generating the detailed PFP drawings and specifications. Details to be completed in EPC. |  | Marine Facilities / Hazard Detection/ Hazard Control/ Fire Protection/ESD
95 | Prior to construction of final design, Commonwealth shall file an evaluation and associated specifications, drawings, and datasheets for transformers demonstrating how it would prevent cascading damage of transformers (e.g., fire walls or spacing) in accordance with NFPA 850 (2015 edition) or approved equivalent. | No | Technip | Owner |  | Technip to provide an evaluation and associated specifications, drawings, and datasheets for transformers. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Barricade will be shown in EPC phase |  |  | Hazard Detection/ Hazard Control/ Fire Protection/ESD
96 | Prior to construction of final design, Commonwealth shall file facility plan drawings showing the proposed location of the firewater and any foam systems. Plan drawings shall clearly show the location of firewater and foam piping, post indicator and sectional valves, and the location and area covered by, each monitor, hydrant, hose, water curtain, deluge system, foam system, water-mist system, and sprinkler. The drawings shall demonstrate that each process area, fire zone, or other sections of piping with several users can be isolated with post indicator or sectional valves and that firewater coverage is provided by at least two monitors or hydrants with sufficient firewater flow to cool exposed surfaces subjected to a fire. The drawings shall also include piping and instrumentation diagrams of the firewater and foam systems. | No | Technip | Owner |  | Technip to provide facility plan drawings showing the proposed location of the firewater and any foam systems. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Firewater System Layouts | Fire Water System Layouts and FW P&IDs will be issued in this Phase. (T.EN - Edgar) Confirm if coverage drawings shall be issued too? Timing for both (Edgar) |  | Hazard Detection/ Hazard Control/ Fire Protection/ESD
97 | Prior to construction of final design, Commonwealth shall specify that the firewater pump shelter is designed to remove the largest firewater pump or other component for maintenance with an overhead or external crane. | No | Technip | Owner |  | Technip to specify in the final design that the firewater pump shelter is designed to remove the largest firewater pump or other component for maintenance with an overhead or external crane. | Owner to reference Condition in appropiate Final Design Implementation Plan and reference documents in which compliance is demonstrated. | CSA will specify the shelter design. Noted in F&S Spec Rev 4 | T.EN - F&S will coordinate with CSA in this Phase for the shelter design. |  | Hazard Detection/ Hazard Control/ Fire Protection/ESD
98 | Prior to construction of final design, Commonwealth shall demonstrate that the firewater storage tank is in compliance with NFPA 22 (2018 edition) or approved equivalent. | No | Technip | Owner |  | Technip to demonstrate that the firewater storage tank is in compliance with NFPA 22 (2018 edition) or approved equivalent. | Owner to reference Condition in appropiate Final Design Implementation Plan and reference documents in which compliance is demonstrated. | Firewater Demand Calculation | Fire Water Demand Calculation will be issued in this Phase to confirm the capacity. T.EN - Mech will issue the DS in this Phase. |  | Hazard Detection/ Hazard Control/ Fire Protection/ESD
99 | Prior to construction of final design, Commonwealth shall specify that the firewater flow test meter is equipped with a transmitter and that a pressure transmitter is installed upstream of the flow transmitter. The flow transmitter and pressure transmitter shall be connected to the DCS and recorded. | No | Technip | Owner |  | Technip to specify in the final design that the firewater flow test meter is equipped with a transmitter and that a pressure transmitter is installed upstream of the flow transmitter. The flow transmitter and pressure transmitter shall be connected to the DCS and recorded. | Owner to reference Condition in appropiate Final Design Implementation Plan and reference documents in which compliance is demonstrated. | Firewater Pump P&IDs. | FW P&IDs will be issued in this Phase. T.EN - Edgar. |  | Hazard Detection/ Hazard Control/ Fire Protection/ESD
100 | Prior to construction of final design, Commonwealth shall file drawings of the storage tank piping support structure and support of horizontal piping at grade including pump columns, relief valves, pipe penetrations, instrumentation, and appurtenances. | No | Technip | Owner |  | Technip to provide drawings of the storage tank piping support structure and support of horizontal piping at grade including pump columns, relief valves, pipe penetrations, instrumentation, and appurtenances. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Information to close will be issued from subcontractor in EPC phase of the project |  |  | LNG Tanks
101 | Prior to construction of final design, Commonwealth shall file the structural analysis of the LNG storage tank and outer containment demonstrating they are designed to withstand all loads and combinations, including shipping loads. | No | Technip | Owner |  | Technip to provide the structural analysis of the LNG storage tank and outer containment demonstrating they are designed to withstand all loads and combinations, including shipping loads. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Information to close will be issued from subcontractor in EPC phase of the project |  |  | LNG Tanks
102 | Prior to construction of the final design, Commonwealth shall file the finalized projectile/missile impact analysis to demonstrate that the outer concrete container wall of the full containment LNG storage tank could withstand projectile/missile impact. The analysis shall detail the projectile/missile speeds and characteristics and methods used to determine penetration resistance and perforation depths. The finalized projectile/missile impact analysis shall be stamped and sealed by the professional engineer-of-record, registered in the State of Louisiana. | No | Technip | Owner |  | Technip to provide the finalized PE stamped and sealed projectile/missile impact analysis. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Information to close will be issued from subcontractor in EPC phase of the project |  |  | LNG Tanks
103 | Prior to construction of final design, Commonwealth shall file an analysis of the structural integrity of the outer containment of the full containment LNG storage tank demonstrating it can withstand the radiant heat from a roof tank top fire or adjacent tank roof fire. | No | Technip | Owner |  | Technip to provide an analysis of the structural integrity of the outer containment of the full containment LNG storage tank demonstrating it can withstand the radiant heat from a roof tank top fire or adjacent tank roof fire. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Information to close will be issued from subcontractor in EPC phase of the project |  |  | LNG Tanks
104 | Prior to construction of final design, Commonwealth shall file an analysis of the structural integrity of the outer containment of the full containment LNG storage tank demonstrating it can withstand the thermal shock caused by a failure of the inner tank. | No | Technip | Owner |  | Technip to provide an analysis of the structural integrity of the outer containment of the full containment LNG storage tank demonstrating it can withstand the thermal shock caused by a failure of the inner tank. | Owner to review, format as necessary and file with FERC in appropriate Final Design Implementation Plan(s). | Information to close will be issued from subcontractor in EPC phase of the project |  |  | LNG Tanks
105 | Prior to commissioning, Commonwealth shall file a detailed schedule for commissioning through equipment startup. The schedule shall include milestones for all procedures and tests to be completed: prior to introduction of hazardous fluids and during commissioning and startup. Commonwealth shall file documentation certifying that each of these milestones has been completed before authorization to commence the next phase of commissioning and startup will be issued. | No | Technip | Owner |  | Technip to provide a detailed schedule for commissioning through equipment startup. | Owner to review, format as necessary and file with FERC in appropriate Commissioning Implementation Plan(s). |  |  |  | Commissioning
106 | Prior to commissioning, Commonwealth shall file detailed plans and procedures for: testing the integrity of onsite mechanical installation; functional tests; introduction of hazardous fluids; operational tests; and placing the equipment into service. | No | Technip | Owner |  | Technip to provide detailed plans and procedures for: testing the integrity of onsite mechanical installation; functional tests; introduction of hazardous fluids; operational tests; and placing the equipment into service. | Owner to review, format as necessary and file with FERC in appropriate Commissioning Implementation Plan(s). | Part of the commisioning plan to be developed in EPC phase |  |  | Commissioning
107 | Prior to commissioning, Commonwealth shall file settlement results from the hydrostatic tests of the LNG storage containers and shall file a plan to periodically verify settlement is as expected and does not exceed the applicable criteria set forth in API 620 (12th edition), API 625 (1st edition), API 650 (13th edition), API 653 (5th edition), and ACI 376 (2011 edition) or approved equivalents. The program shall also specify what actions would be taken after various levels of seismic events. | No | Technip | Owner |  | Technip to provide settlement results from the hydrostatic tests of the LNG storage containers and a plan to periodically verify settlement. The program shall also specify what actions would be taken after various levels of seismic events. | Owner to review, format as necessary and file with FERC in appropriate Commissioning Implementation Plan(s). | To be developed with the tank vendor in the EPC phase |  |  | Commissioning
108 | Prior to commissioning, Commonwealth shall file the operation and maintenance procedures and manuals, as well as safety procedures, hot work procedures and permits, abnormal operating conditions reporting procedures, simultaneous operations procedures, and management of change procedures and forms. | No | Technip | Owner |  | Technip to provide operation and maintenance procedures and manuals, as well as safety procedures, hot work procedures and permits, abnormal operating conditions reporting procedures, simultaneous operations procedures, and management of change procedures and forms. | Owner to review, format as necessary and file with FERC in appropriate Commissioning Implementation Plan(s). | Part of the commisioning plan to be developed in EPC phase |  |  | Commissioning
109 | Prior to commissioning, Commonwealth shall file a plan for clean-out, dry-out, purging, and tightness testing. This plan shall address the requirements of the American Gas Association’s Purging Principles and Practice and shall provide justification if not using an inert or non-flammable gas for clean-out, dry-out, purging, and tightness testing. | No | Technip | Owner |  | Technip to provide a plan for clean-out, dry-out, purging, and tightness testing. | Owner to review, format as necessary and file with FERC in appropriate Commissioning Implementation Plan(s). | Part of the commisioning plan to be developed in EPC phase |  |  | Commissioning
110 | Prior to commissioning, Commonwealth shall tag all equipment, instrumentation, and valves in the field, including drain valves, vent valves, main valves, and carsealed or locked valves. | No | Technip | Owner |  | Technip to tag all equipment, instrumentation, and valves in the field, including drain valves, vent valves, main valves, and carsealed or locked valves. | Owner to reference Condition in appropiate Commissioning Implementation Plan and reference documents in which compliance is demonstrated. | EPC |  |  | Commissioning
111 | Prior to commissioning, Commonwealth shall file a plan to maintain a detailed training log to demonstrate that operating, maintenance, and emergency response staff have completed the required training. | No | Owner | Technip |  | Owner to file with FERC a plan to maintain a detailed training log to demonstrate that CWLNG operating, maintenance, and emergency response staff have completed the required training. | Technip to ensure that training logs are maintained through construction, commissioning and start-up to demonstrate that operating, maintenance, and emergency response staff have completed the required training. Training logs should be made available for FERC review if requested. | operation handover plan to be done in EPC phase |  |  | Commissioning
112 | Prior to commissioning, Commonwealth shall file the procedures for pressure/leak tests which address the requirements of American Society of Mechanical Engineers (ASME) Boiler and Pressure Vessel Code Section VIII (2017 edition) and ASME B31.3 (2016 edition) or approved equivalents. In addition, Commonwealth shall file a line list of pneumatic and hydrostatic test pressures. | No | Technip | Owner |  | Technip to provide the procedures for pressure/leak tests and a line list of pneumatic and hydrostatic test pressures. | Owner to review, format as necessary and file with FERC in appropriate Commissioning Implementation Plan(s). | Part of the commisioning plan to be developed in EPC phase |  |  | Commissioning
113 | Prior to introduction of hazardous fluids, Commonwealth shall complete and document a pre-startup safety review to ensure that installed equipment meets the design and operating intent of the facility. The pre-startup safety review shall include any changes since the last hazard review, operating procedures, and operator training. A copy of the review with a list of recommendations, and actions taken on each recommendation, shall be filed. | No | Technip | Owner |  | Technip to complete and document a pre-startup safety review and provide a copy of the review with a list of recommendations, and actions taken on each recommendation. | Owner to review, format as necessary and file with FERC in appropriate Hazardous Fluids Implementation Plan(s). | EPC |  |  | Hazardous Fluids
114 | Prior to introduction of hazardous fluids, Commonwealth shall complete and document all pertinent tests (Factory Acceptance Tests, Site Acceptance Tests, Site Integration Tests) associated with the DCS and SIS that demonstrates full functionality and operability of the system. | No | Technip | Owner |  | Technip to complete and document all pertinent tests (Factory Acceptance Tests, Site Acceptance Tests, Site Integration Tests) associated with the DCS and SIS that demonstrates full functionality and operability of the system. | Owner to reference Condition in appropiate Hazardous Fluids Implementation Plan. | Part of the commisioning plan to be developed in EPC phase |  |  | Hazardous Fluids
115 | Prior to introduction of hazardous fluids, Commonwealth shall develop, file, and implement an alarm management program consistent with ISA 18.2 (2016 edition) or approved equivalent to reduce alarm complacency and maximize the effectiveness of operator response to alarms. | No | Technip | Owner |  | Technip to develop, provide and implement an alarm management program. | Owner to review, format as necessary and file with FERC in appropriate Hazardous Fluids Implementation Plan(s). | developed with Fire & Safety in EPC |  |  | Hazardous Fluids
116 | Prior to introduction of hazardous fluids, Commonwealth shall complete and document a clean agent acceptance tests. | No | Technip | Owner |  | Technip to complete and document a clean agent acceptance tests. | Owner to reference Condition in appropiate Hazardous Fluids Implementation Plan. | Part of the commisioning plan to be developed in EPC phase |  |  | Hazardous Fluids
117 | Prior to introduction of hazardous fluids, Commonwealth shall complete and document a firewater pump acceptance test and firewater monitor and hydrant coverage test. The actual coverage area from each monitor and hydrant shall be shown on facility plot plan(s). | No | Technip | Owner |  | Technip to complete and document a firewater pump acceptance test and firewater monitor and hydrant coverage test. The actual coverage area from each monitor and hydrant shall be shown on facility plot plan(s). | Owner to reference Condition in appropiate Hazardous Fluids Implementation Plan. | developed with Fire & Safety in EPC |  |  | Hazardous Fluids
118 | Prior to introduction of hazardous fluids, Commonwealth shall complete and document foam system and sprinkler system acceptance tests. | No | Technip | Owner |  | Technip to complete and document foam system and sprinkler system acceptance tests. | Owner to reference Condition in appropiate Hazardous Fluids Implementation Plan. | developed with Fire & Safety in EPC |  |  | Hazardous Fluids
119 | Commonwealth shall file a request for written authorization from the Director of OEP prior to unloading or loading the first LNG commissioning cargo. After production of first LNG, Commonwealth shall file weekly reports on the commissioning of the proposed systems that detail the progress toward demonstrating the facilities can safely and reliably operate at or near the design production rate. The reports shall include a summary of activities, problems encountered, and remedial actions taken. The weekly reports shall also include the latest commissioning schedule, including projected and actual LNG production by each liquefaction train, LNG storage inventories in each storage tank, and the number of anticipated and actual LNG commissioning cargoes, along with the associated volumes loaded or unloaded. Further, the weekly reports shall include a status and list of all planned and completed safety and reliability tests, work authorizations, and punch list items. Problems of significant magnitude shall be reported to the FERC within 24 hours. | No | Owner | Technip |  | Technip to support Owner with information required for the weekly reports. | Owner to reference Condition and request written authorization from the Director of OEP prior to unloading or loading the first LNG commissioning cargo. After production of first LNG Owner will file weekly reports. Significant problems reported to FERC within 24 hours. |  |  |  | Commissioning
120 | Prior to commencement of service, Commonwealth shall file a request for written authorization from the Director of OEP. Such authorization would only be granted following a determination by the USCG, under its authorities under the Ports and Waterways Safety Act, the Magnuson Act, the Maritime Transportation Security Act of 2002, and the Security and Accountability For Every Port Act, that appropriate measures to ensure the safety and security of the facility and the waterway have been put into place by Commonwealth or other appropriate parties. | No | Owner | Technip |  | Technip to support Owner to ensure appropriate safety and security measures have been put into place. | Owner to file request for written authorization to commence service. |  |  |  | Commence Service
121 | Prior to commencement of service, Commonwealth shall file any proposed revisions to the security plan and physical security of the plant. | No | Technip | Owner |  | Technip to provide any proposed revisions to the security plan and physical security of the plant. | Owner to file any proposed revisions in Commencement of Service authorization request. |  |  |  | Commence Service
122 | Prior to commencement of service, Commonwealth shall label piping with fluid service and direction of flow in the field consistent with ASME A13.1 (2007 edition) or approved equivalent, in addition to the pipe labeling requirements of NFPA 59A (2001). | No | Technip | Owner |  | Technip to label piping with fluid service and direction of flow in the field. | Owner to reference Condition in Commencement of Service authorization request. | EPC |  |  | Commence Service
123 | Prior to commencement of service, Commonwealth shall provide plans for any preventative and predictive maintenance program that performs periodic or continuous equipment condition monitoring. | No | Technip | Owner |  | Technip to provide plans for any preventative and predictive maintenance program that performs periodic or continuous equipment condition monitoring. | Owner to reference Condition in Commencement of Service authorization request. |  |  |  | Commence Service
In addition, conditions 124 through 127 shall apply throughout the life of the LNG Terminal facilities:
124 | Prior to commencement of service, Commonwealth shall develop procedures for offsite contractor’s responsibilities, restrictions, monitoring, training, and limitations and for supervision of these contractors and their tasks by Commonwealth staff. Specifically, the procedures shall address: a. selecting a contractor, including obtaining and evaluating information regarding the contract employer’s safety performance and programs; b. informing contractors of the known potential hazards, including flammable and toxic release, explosion, and fire, related to the contractor's work and systems they are working on; c. developing and implementing provisions to control and monitor the entrance, presence, and exit of contract employers and contract employees from process areas, buildings, and the plant; d. developing and implementing safe work practices for control of personnel safety hazards, including lockout/tagout, confined space entry, work permits, hot work, and opening process equipment or piping; e. developing and implementing safe work practices for control of process safety hazards, including identification of layers of protection in systems being worked on, recognizing abnormal conditions on systems they are working on, and re-instatement of layers of protection, including ensuring bypass, isolation valve, and car-seal programs and procedures are being followed; f. developing and implementing provisions to ensure contractors are trained on the emergency action plans and that they are accounted for in the event of an emergency; and g. monitoring and periodically evaluating the performance of contract employers in fulfilling their obligations above, including successful and safe completion of work and re-instatement of all layers of protection. | No | Owner | NA |  | None | Owner to reference Condition in Commencement of Service authorization request. | EPC |  |  | Commence Service
125 | The facility shall be subject to regular FERC staff technical reviews and site inspections on at least an annual basis or more frequently as circumstances indicate. Prior to each FERC staff technical review and site inspection, Commonwealth shall respond to a specific data request including information relating to possible design and operating conditions that may have been imposed by other agencies or organizations. Up-to-date detailed P&IDs reflecting facility modifications and provision of other pertinent information not included in the semi-annual reports described below, including facility events that have taken place since the previously submitted semi-annual report, shall be submitted. | No | Owner | Technip |  | Technip to support Owner during construction and commissioning inspections as required. Technip would support Owner with Operations inspections only if there are open mitigation measures that were not satisfied after Owner receives In-Service authorization or for any other reasons under the EPC Agreement. | Life of Facility Condition for Owner. Owner to file compliance statement in General Conditions Implementation Plan. Includes response to specific data request on possible design and operation conditions imposed by other agencies. |  | CWLNG to coordinate with FERC and TEN to arrange site inspections as required |  | General Conditions
126 | Semi-annual operational reports shall be filed with the Secretary to identify changes in facility design and operating conditions; abnormal operating experiences; activities (e.g., ship arrivals, quantity and composition of imported and exported LNG, liquefied and vaporized quantities, boil off/flash gas); and plant modifications, including future plans and progress thereof. Abnormalities shall include, but not be limited to, unloading/loading/shipping problems, potential hazardous conditions from offsite vessels, storage tank stratification or rollover, geysering, storage tank pressure excursions, cold spots on the storage tank, storage tank vibrations and/or vibrations in associated cryogenic piping, storage tank settlement, significant equipment or instrumentation malfunctions or failures, nonscheduled maintenance or repair (and reasons therefore), relative movement of storage tank inner vessels, hazardous fluids releases, fires involving hazardous fluids and/or from other sources, negative pressure (vacuum) within a storage tank, and higher than predicted boil off rates. Adverse weather conditions and the effect on the facility also shall be reported. Reports shall be submitted within 45 days after each period ending June 30 and December 31. In addition to the above items, a section entitled “Significant Plant Modifications Proposed for the Next 12 Months (dates)” shall be included in the semi-annual operational reports. Such information would provide the FERC staff with early notice of anticipated future construction/maintenance at the LNG facilities. | No | Owner | NA |  | None | Life of Facility Condition for Owner. Owner to file semi-annual operational reports. Owner will also file compliance statement with General Conditions Implementation Plan. Includes abnormalities and planned schedule modifications proposed next 12 months. |  |  |  | General Condition
127 | In the event the temperature of any region of the LNG storage container, including any secondary containment and imbedded pipe supports, becomes less than the minimum specified operating temperature for the material, the Commission shall be notified within 24 hours and procedures for corrective action shall be specified. | No | Owner | Technip |  | Technip to support Owner as required after LNG is introduced into LNG Storage Tank until Technip responsibility ends as defined in the EPC Agreement. | Life of Facility Condition for Owner. Owner to notify FERC within 24 hours. Owner will file compliance statement in General Conditions Implementation Plan. |  |  |  | General Condition
128 | Significant non-scheduled events, including safety-related incidents (e.g., LNG, condensate, refrigerant, or natural gas releases; fires; explosions; mechanical failures; unusual over pressurization; and major injuries) and security-related incidents (e.g., attempts to enter site, suspicious activities) shall be reported to the FERC staff. In the event that an abnormality is of significant magnitude to threaten public or employee safety, cause significant property damage, or interrupt service, notification shall be made immediately, without unduly interfering with any necessary or appropriate emergency repair, alarm, or other emergency procedure. In all instances, notification shall be made to the FERC staff within 24 hours. This notification practice shall be incorporated into the LNG plant’s emergency plan. Examples of reportable hazardous fluids-related incidents include the following: a. fire; b. explosion; c. estimated property damage of $50,000 or more; d. death or personal injury e. release of hazardous fluids for five minutes or more; f. unintended movement or abnormal loading by environmental causes, such as an earthquake, landslide, or flood, that impairs the serviceability, structural integrity, or reliability of an LNG facility that contains, controls, or processes hazardous fluids; g. any crack or other material defect that impairs the structural integrity or reliability of an LNG facility that contains, controls, or processes hazardous fluids; h. any malfunction or operating error that causes the pressure of a pipeline or LNG facility that contains or processes hazardous fluids to rise above its maximum allowable operating pressure (or working pressure for LNG facilities) plus the build-up allowed for operation of pressure-limiting or control devices; i. a leak in an LNG facility that contains or processes hazardous fluids that constitutes an emergency; j. inner tank leakage, ineffective insulation, or frost heave that impairs the structural integrity of an LNG storage tank; k. any safety-related condition that could lead to an imminent hazard and cause (either directly or indirectly by remedial action of the operator), for purposes other than abandonment, a 20 percent reduction in operating pressure or shutdown of operation of a pipeline or an LNG facility that contains or processes hazardous fluids; l. safety-related incidents to hazardous fluids transportation occurring at or en route to and from the LNG facility; or m. an event that is significant in the judgment of the operator and/or management even though it did not meet the above criteria or the guidelines set forth in an LNG facility’s incident management plan. In the event of an incident, the Director of OEP has delegated authority to take whatever steps are necessary to ensure operational reliability and to protect human life, health, property, or the environment, including authority to direct the LNG Facility to cease operations. Following the initial company notification, the FERC staff will determine the need for a separate follow-up report or follow up in the upcoming semi-annual operational report. All company follow-up reports shall include investigation results and recommendations to minimize a reoccurrence of the incident. (Final EIS section 4.13.1) | No | Owner | Technip |  | Technip to support Owner throughout Project until their responsibility ends as defined in the EPC Agreement. | Life of Facility Condition for Owner. Owner to notify FERC immediately or within 24 hours. Owner to file compliance statement in General Conditions Implementation Plan. |  |  |  | General Condition

## Condition 41 (hidden)
| Referenced IP Vol. # | Method of Receipt | Date Received (Unique ID) | Request No. (Child) | Classification | Discipline | Related Condition | Related IP Package | Related EIR | Topic | Related EIR Received/Response Date | FERC Order Condition | Received EIR Language | CWLNG Individual Assigned | Technip Individual Assigned | Target Response Date | Actual Response Date | EIR Response Summary | Document File Name | Document Number | Status | Column1
124. 3/4/2020 | N/A | Docket | 2020-01-02 | [6 empty] | Fire and Safety | N/A | 41 | The fire and safety philosophy (078051C-000-CN-1930-0002) in Appendix 13.B.2 indicates low expansion foam would be used where determined in the fire hazard analysis. In addition, the preliminary fire protection evaluation in Appendix 13.S.1 does not mention low expansion foam anywhere, only high expansion foam and drawings 078051C-000-DW-1933-0200 and 078051C-000-DW-1933-0212 in Appendix 13.S.10 show no foam system in the truck unloading area. Low expansion foam has been shown to be effective at suppressing heavier hydrocarbon fires, such as those from condensates. Explain why low expansion foam is not proposed for condensate fires to prevent cascading impacts. |  |  |  |  | Commonwealth will file a response by March 4, 2020. | fire and safety philosophy high expansion foam drawings | (078051C-000-CN-1930-0002) 078051C-000-DW-1933-0200 078051C-000-DW-1933-0212
| N/A | Docket | 2020-01-02 | [6 empty] | Fire and Safety | 2020-03-04 | 41 | The fire and safety philosophy (078051C-000-CN-1930-0002) in Appendix 13.B.2 indicates low expansion foam would be used where determined in the fire hazard analysis. In addition, the preliminary fire protection evaluation in Appendix 13.S.1 does not mention low expansion foam anywhere, only high expansion foam and drawings 078051C-000-DW-1933-0200 and 078051C-000-DW-1933-0212 in Appendix 13.S.10 show no foam system in the truck unloading area. Low expansion foam has been shown to be effective at suppressing heavier hydrocarbon fires, such as those from condensates. Explain why low expansion foam is not proposed for condensate fires to prevent cascading impacts. |  |  |  |  | As illustrated on Drawing 078051C-000-DW-1933-0211, NOTE 5, low expansion foam will be utilized for flammable liquids, and monitorsadditional areas will be evaluated during final design to address the appropriate will be provided with foam totes. These will be included near the condensate storage area. The use of low expansion foam in additional areas will be evaluated during final design to address the appropriate hydrocarbon hazards.
15. 2/4/2020 | N/A | Docket | 2020-01-02 | [6 empty] | LNG Tank vacuum relief | 2020-02-04 | 41 | P&ID 15803-PI-2000-200 in Appendix 13.E.5 shows the LNG storage tanks vacuum relief valves and pressure relief valves for the tank; however, a discretionary vent is not shown. Indicate if a discretionary vent would be provided on the LNG storage tanks with an isolation valve to allow for maintenance that is Car Sealed Open (CSO). |  |  |  |  | A discretionary vent will be provided on each LNG tank with an isolation valve to allow for maintenance that is Car Sealed Open (“CSO”). The vent would be to the atmosphere and would be operated through the distributed control system (“DCS”). The P&ID (LNG Storage Tank T-2000A, Piping and Instrumentation Diagram,15803-PI-2000-200_Rev 3)has been updated and is provided as Attachment Q015&016 (CUI/CEII-Critical Energy Infrastructure Information-Do Not Release). | P&ID (LNG Storage Tank T-2000A, Piping and Instrumentation Diagram | 15803-PI-2000-200_Rev 3
45. 2/4/2020 | N/A | Docket | 2020-01-02 | [6 empty] | flow from refrigerant delivery trucks | 2020-02-04 | 41 | P&IDs 078051C-060-PID-0031-0002/0007/00013 show valves XV-169/168/100 would shut off the flow from the refrigerant delivery trucks for the ethylene, propane and isopentane, respectively. While exact distances may not be known at this stage of the design, explain how far from the truck unloading skid these valves would be located to ensure that potential hazardous events would not inhibit the use of these valves or clarify whether these valves would be firesafe and indicate what standards and duration they would be rated. |  |  |  |  | The current design has the refrigerant storage tanks (ethylene, propane, and isopentane) all located inside the storm surge wall, while the truck unloading station is located outside the wall. The unloading shutoff valves XV-169/168/100 will be located outside the wall. At this time, the precise location of these shutoff valves has not been pinpointed, nor have the valves been selected. Emergency shut-off valves will typically be located 50 feet from the source of a release to allow access during an emergency. If the valves must be placed closer than 50 feet, Commonwealth will specify a fire safe design, fireproof the valves (if within 30 feet) and provide remote actuation via a DCS switch and local panel switch located 50 feet from the source of potential release.
65. 2/4/2020 | N/A | Docket | 2020-01-02 | [6 empty] | Isolation philosopy | 2020-02-04 | 41 | P&ID 15803-PI-0000-0007 in Appendix 13.E.5 provides PSV arrangement diagrams for a portion of the OSBL P&IDs. The arrangements shown in diagrams 3621 and 9021 do not appear to align with the isolation valve philosophy outlined in the Isolation Philosophy (078051C-000-CN-0008-0002 in Appendix 13.B) which has been applied across the ISBL P&IDs. For example, the ISBL P&IDs show double block and bleed arrangements on the inlet to PSVs which protect vessels of higher-pressure classes; however, none of the detailed arrangements shown on 15803-PI-0000-0007 utilized a double block and bleed. Explain if the OSBL systems would be redesigned to follow the Isolation Philosophy outlined in 078051C-000-CN-0008-0002. |  |  |  |  | The OSBL system will be redesigned during final design to follow the same Isolation Philosophy (Document number: 078051C-000-CN-0008-0002) included in Appendix 13.B. The P&IDs (along with legend and detail sheets) will also be made consistent during final design. | Isolation Philosophy Appendix 13.B | 078051C-000-CN-0008-0002
106. 2/4/2020 | N/A | Docket | 2020-01-02 | [6 empty] | Vapor tight buildings | 2020-02-04 | 41 | Drawing 07850C-000-DW-1920-0001 in Appendix 13.N.5 shows the Electrical Area Classifications of the liquefaction and pretreatment modules at grade level. These drawings show the hazardous area “wrapping” around the MCC Building -01 and -02. Per the codes, this is acceptable if the structure is vapor impervious. Indicate whether the buildings would be vapor tight and explain the materials of construction of the MCC buildings or other means that would be used (e.g., pressurization) to ensure they would be vapor tight. Also explain the location of the doors for MCC Buildings -01 and -02. |  |  |  |  | The MCC Building walls facing the hazardous areas will not have any doors, windows, or other permeable openings and therefore will be vapor impervious. Doors not facing the hazardous areas will have air-tight weatherstripping as recommended by API RP500. All man and equipment doors will be located on the general purpose side(s) of the building. Doors are placed for egress from either end of a long line-up of switchgear or MCC. Final placement will be determined during the detailed design phase.
125c. 3/4/2020 | N/A | Docket | 2020-01-02 | [6 empty] | Fire and Safety | 2020-03-04 | 41 | Maintenance building drawings A2.2-01 and A2.2-02 in Appendix 13.M.8 show two separate chemical storage rooms c. Explain how the facility would prevent future storage of materials in this space which would cause the hazard category to increase, thereby resulting in a potentially undersized sprinkler system. |  |  |  |  | Administrative controls and procedures will be developed during detail design to prevent improper use of the storage rooms.
127. 3/4/2020 | N/A | Docket | 2020-01-02 | [6 empty] | Fire and Safety | 2020-03-04 | 41 | Section 8.1.5 of the Fire and Safety Philosophy (078051C-000-CN-1930-0002 in Appendix 13.B) states that post indicator valves (PIVs) would be placed such that closure of a PIV would not cut off no more than 6 take off connections for hydrants, monitors or water spray systems. In addition, the philosophy states that water spray and deluge systems shall be fed from two separate segments of the firewater distribution system to ensure supply availability. However, the P&IDs and other drawings indicate multiple scenarios where significant portions of the firewater system would need to be isolated from service in order to address leaks. Explain if the firewater loop design would be updated to add additional PIVs to ensure significant portions of the firewater coverage throughout the facility would not need to be isolated during maintenance. |  |  |  |  | Firewater loop design will be updated to add additional PIVs to ensure significant portions of the firewater coverage throughout the acility would not need to be isolated during maintenance. The design, layouts, and subsequent P&IDs will be updated during final design to be consistent with the Fire and Safety Philosophy, minimizing the quantity of equipment inoperable at any time due to failure or maintenance. Drawings will also show deluge skids provided with two water supplies. | Fire and Safety Philosophy Appendix 13.B | 078051C-000-CN-1930-0002
134. 3/4/2020 | N/A | Docket | 2020-01-02 | [6 empty] | Fire and Safety | 2020-03-04 | 41 | Firewater P&ID 078051C-000-PID-1931-0091 in Appendix 13.S.10 shows only a single check valve and siphon break isolating the freshwater supply from the firewater tank. Section 13.38.1.3 in Resource Report 13 states that the firewater storage tank would be filled from the municipal water supply. Explain if a single isolation valve and siphon break would meet the local code requirements of isolating this system from the municipal water supply. |  |  |  |  | The design currently includes a check valve and a siphon break on the inlet line. A backflow preventor and physical break will be added during final design. Minimum State and local requirements will be verified and compliance will be confirmed during final design, in accordance with NFPA 22. | Firewater P&ID | 078051C-000-PID-1931-0091
135. 3/4/2020 | N/A | Docket | 2020-01-02 | [6 empty] | Fire and Safety | 2020-03-04 | 41 | Section 13.35.1.2 in Resource Report 13 states that steel support structure elements subject to cryogenic spills would be treated with structural protection and refers to Appendix 13.S.4 for drawings depicting areas with cryogenic protection. However, these drawings only discuss the need for structural fire proofing. Explain if these areas would have a combination cryogenic and fireproof structural protection. Also explain what codes and standards the passive cryogenic protection product would follow. |  |  |  |  | Cryogenic spill protection intumescent material with dual function (cryogenic spill and fire protection) would be used. Testing of the material would be conformed with ISO 20088-1: 2018 "Determination of the resistance to cryogenic spillage of insulation material". Charteck 1620CSP or equivalent material would be used. | Resource Report 13 Section 13.35.1.2
148. 3/4/2020 | N/A | Docket | 2020-01-02 | [6 empty] | Gas Detection | 2020-03-04 | 41 | Drawing 078051C-000-DW-1950-0407 in Appendix 13.S.6 shows the hazard detection of train A at the 200 foot elevation. This drawing shows no gas detectors along the perimeter of the aerial coolers. Explain how a gas leak from the aerial coolers would be detected. |  |  |  |  | Open Path gas detectors will be placed along the catwalk below the air coolers. Drawing 078051C-000-DW-1950-0407 will be updated in Final Design to reflect this equipment. | Appendix 13.S.6 | 078051C-000-DW-1950-0407
153. 3/4/2020 | N/A | Docket | 2020-01-02 | [6 empty] | Hazard Detection | 2020-03-04 | 41 | Appendix 13.S.2 lists the various impoundment areas at the proposed facility. However, some of these impoundment areas are not listed in Appendix 13.S.5 as having sump pumps that would shut down upon activation of the hazard detectors. For the following impoundment locations, indicate whether a sump pump would be present in the impoundment/dike and whether the existing hazard detectors (listed in parentheses below) would trigger a shutdown of the sump pump if hazardous releases are detected. a. Truck Loading/ Unloading Area, S-4101 (gas and flame detectors) b. Refrigerant Storage Area, S-4116 (gas and flame detectors) c. Condensate Storage Area, D-1 (gas and flame detectors) d. Tank Farm Area, D-2 (flame detectors) |  |  |  |  | A sump pump would be provided for: a. Truck Loading/ Unloading Area, S-4101 b. Refrigerant Storage Area, S-4116 c. Condensate Storage Area, D-1 d. Tank Farm Area, D-2. Activation of low temperature, gas and/or flame detectors in the area or in the sump will shut down the sump pumps. Document inconsistencies will be updated in final design to reflect this change. | Appendix 13.S.2 Appendix 13.S.5
154. 3/4/2020 | N/A | Docket | 2020-01-02 | [6 empty] | Fire and Safety | 2020-03-04 | 41 | Appendix 13.S.5 lists various types of fire detection in buildings throughout the plant. For the buildings listed below, explain why fire detection (e.g., smoke, flame, etc.) would not be provided. a. Maintenance Building b. PTF MCC c. Liquefaction MCC d. PTF Analyzer Building e. Liquefaction Facility Analyzer Building f. PTF RIE Building g. Liquefaction RIE Building |  |  |  |  | Manual pull stations, smoke detection, and combustible gas detection would be provided for the Maintenance Building, PTF MCC, Liquefaction MCC, PTF Analyzer Building, Liquefaction Facility Analyzer Building, PTF RIE Building, and the Liquefaction RIE Building. Associated documentation will be updated in Final Design to reflect this equipment. | Appendix 13.S.5
155. 3/4/2020 | N/A | Docket | 2020-01-02 | [6 empty] | Fire and Safety | 2020-03-04 | 41 | In Appendix 13.S.5, two flame detectors are listed for each protected area/equipment. This doubling up of flame detectors allows for a level of redundancy and would allow for voting logic, as stated in Appendix 13.B.2 on page 24: “Flame detectors will be located to ensure multiple detectors are available for voting where required.” However, there are four instances where an area would have one flame detector. Explain why the following flame detectors would not have a redundant pair like the rest of the flame detectors listed in Appendix 13.S.5. a. BT-A50209, monitoring P-A2601A (Glycol Water Circulation Pumps) b. BT-A50210, monitoring P-A0401A (Debutanizer Reflux Pumps) c. BT-050201, monitoring P-07001B (Acid Gas KO Drum Pumps) d. BT-050202, monitoring A-06601A (OSBL Hot Oil Dump Cooler) |  |  |  |  | Redundant flame detection would be provided for the following equipment: a. P-A2601A (Glycol Water Circulation Pumps) b. P-A0401A (Debutanizer Reflux Pumps) c. P-07001B (Acid Gas KO Drum Pumps) d. A-06601A (OSBL Hot Oil Dump Cooler) Associated documentation will be updated in final design to reflect this equipment. | Appendix 13.S.5
157. 3/4/2020 | N/A | Docket | 2020-01-02 | [6 empty] | Fire and Safety | 2020-03-04 | 41 | The Fire and Safety Philosophy (078051C-000-CN-1930-0002 in Appendix 13.B.2) states: “At a minimum, flame detection shall be provided in areas where flammable liquids are handled, stored, processed or contained within packaged equipment.” Explain why flame detectors are not listed near the Marine Transfer Area (such as the LNG Ship Loading Pumps, Dock Surge Drain Drum Pumps). |  |  |  |  | Flame and gas detection would be provided in the Marine Transfer Area (including the LNG Ship Loading Pumps and Dock Surge Drain Drum Pumps). Associateddocumentation will be updated in final design to reflect this equipment. | Appendix 13.B.2 | 078051C-000-CN-1930-0002
161. 3/4/2020 | N/A | Docket | 2020-01-02 | [6 empty] | Hazard Detection | 2020-03-04 | 41 | Page 25 of Hazard Detection and Mitigation System Standard (15803-TS-0000-006 in Appendix 13.B.1) states: “Heat detectors shall be installed in areas where smoke detectors are not suitable. Specific locations include over fired equipment, in outdoor areas, and within buildings/enclosures where fast growing fires would be likely.” However, Appendices 13.S.5 and 13.S.6 do not show heat detectors, or any type of fire detection, near two pieces of fired equipment: Hot Oil Startup Fired Heater (Z-06601) and Thermal Oxidizer (Z-07002). Explain why heat detectors (or other fire detection devices) would not be provided near this fired equipment. |  |  |  |  | Heat detectors would be provided for the Hot Oil Startup Fired Heater (Z-06601) and Thermal Oxidizer (Z-07002). Associated documentation will be updated in final design to reflect this equipment. | Hazard Detection and Mitigation System Standard Appendix 13.B.1 | 15803-TS-0000-006
162. 3/4/2020 | N/A | Docket | 2020-01-02 | [6 empty] | Hazard Detection | 2020-03-04 | 41 | Appendix 13.S.5 shows that there would be only one high temperature detector for the LNG Tank Area Pipe to Pier location (TE-6101B). The alarm and shutdown function for this high temperature detector states that immediate shutdown would occur if two adjacent detectors alarm, and shutdown would occur after 10 minutes of a continuous single alarm. Describe how the response of requiring two nearby detectors to alarm for shutdown to occur would be appropriate when only one high temperature alarm would be present in this area. |  |  |  |  | The high temperature detector in the LNG Tanks Area Pipe to Pier location was intended to be a low temperature detector. The low temperature detectors will work with the nearby gas detectors to provide a 2ooN voting logic for shutdown to occur. Drawings and lists associated with this detail will be updated during final design. | Appendix 13.S.5
164. 3/4/2020 | N/A | Docket | 2020-01-02 | [6 empty] | Fire and Safety | 2020-03-04 | 41 | Drawing 15803-DG-6200-001-01 in Appendix 13.S.6 shows the entire plant layout with manual pull stations. However, this drawing shows that there would be no manual pull stations near either the feed gas metering station or the opposite end of the LNG Tank Area from MS-6002 (i.e., near Tank A). Explain why manual pull stations would not be provided near these areas. |  |  |  |  | Manual pull stations would be provided near the LNG Tank Fare area and the Feed Gas Metering Station. Associated documentation will be updated in final design to reflect this equipment. | Appendix 13.S.6 | 15803-DG-6200-001-01
165. 3/4/2020 | N/A | Docket | 2020-01-02 | [6 empty] | Fire and Safety | 2020-03-04 | 41 | Appendix 13.S.6 shows the locations of manual alarm call points throughout the pretreatment and liquefaction areas. According to document 078051C-000-DW-1950-0400 in Appendix 13.S.6, there would not be manual alarm call points in close proximity to the following locations. For each location, explain the rationale for not including manual alarm call points. a. MR Compressor area b. Area that includes K-A0402, K-A0401, and Lube Oil Skid c. Ladder access points, as shown in Drawing 078051C-000-DW-0051-0001 in Appendix 13.E.6 |  |  |  |  | Manual pull stations would be provided near the MR Compressor area; the area containing K-A0402, K-A0401, and the Lube Oil Skid; and the ladder access points. Associated documentation will be updated in final design to reflect this equipment. | Appendix 13.S.6 | 078051C-000-DW-1950-0400
167. 3/4/2020 | N/A | Docket | 2020-01-02 | [7 empty] | 2020-03-04 | 41 | Drawing 078051C-000-DW-1950-0401 in Appendix 13.S.6 shows a plot plan with ESD stations marked. a. Page 25 of the Fire and Safety Philosophy (078051C-000-CN-1930-0002 in Appendix 13.B) indicates that ESD field push buttons would be located throughout the facility, and that an operator in the control room would perform the emergency shutdown. Clarify if ESD field push buttons would automatically shutdown the corresponding equipment/unit, or if an operator in the control room must act to shutdown the equipment/unit. If an operator must act to shutdown the equipment/unit, provide justification for this arrangement rather than having the field ESD push buttons trigger a shutdown automatically. b. Instrumentation and Control Standard (15803-TS-0000-007 in Appendix 13.B.2) states that the three levels of facility shutdown would be a total facility shutdown; area shutdown; and equipment (local) shutdown. Update the drawings in Appendix 13.S.6 to indicate which ESD levels would be triggered by each ESD station. c. Page 25 of the Fire and Safety Philosophy (078051C-000-CN-1930-0002 in Appendix 13.B.2) indicates ESD field push buttons would be installed throughout the facility, along normal exit routes, and at other strategic locations in process areas and/or near high hazard equipment or operations. The drawing in Appendix 13.S.6 does not show any ESD stations near the LNG Tank area; the gas turbine/feed gas metering area; or the hot oil fired heater/thermal oxidizer area. Explain why ESD stations would not be located in these areas. |  |  |  |  | none | Appendix 13.S.6 | 078051C-000-DW-1950-0401
7. 6/4/2021 | N/A | Docket | 2020-06-05 | [6 empty] | Fire and Safety | 2021-06-04 | 41 | In response to item 149-b, Commonwealth indicated that fire protection equipment would be relocated to eliminate or at least minimize the potential for hazardous/combustible gas migration into air intakes of critical equipment such as the fire pumps. However, the firewater storage tanks, firewater pumps and emergency diesel generators would also be within the 1 psi overpressure as shown in figure 9 of the Hazard Analysis Report in Appendix 13.H.3. and well within the 1,600 BTU/ft2-hr zone per figure 10.2-2 of the Hazard Analysis Report in Appendix 13.H.3. Explain what the overpressures would be at each of these pieces of equipment following a blast from Scenarios ETH-1V, MR-11c and HC-11V. Confirm that fire protection and emergency equipment would be located away, or protected, from flammable vapor, overpressures, and high radiant heat. Describe the criteria that Commonwealth uses to determine that this equipment would be located in a nonhazardous location or would be adequately protected. If this equipment is relocated, provide a revised plot plan. If this equipment is not relocated, explain what level of radiant heat and overpressure each of these critical pieces of equipment is able to withstand and still perform their safety function. |  |  |  |  | The Project will locate fire protection and emergency equipment away from potential flammable vapor, overpressures, and high radiant heat such that the equipment will be available in the event of a Facility emergency. During Final Design, the firewater storage tanks, firewater pumps, and emergency diesel generators will be specified to withstand, while still performing their safety function, the maximum potential overpressure and radiant heat level that may be experienced in their final location. Passive features, such as blast walls, or active features such as water sprays may be added to the design to ensure protection and continued operation of the equipment. The primary firewater pumps (P-6002 & P-6003A/B/C) will be supplied inside enclosures and along with the emergency generator are located at the north end of the Facility away from any Process Areas or equipment. The enclosure that houses the secondary firewater lift pumps (P-6005 & P-6006) is located at the southeast area of the plot, outside of the facilities concrete wall. These have been located to minimize the potential for any impacts from flammable vapor migration, overpressures, and high radiant heat. All firewater pump enclosures will be protected by sprinkler systems and located in non-classified areas. Reference documents include the Fire & Safety Philosophy and Fire Water System Layouts, provided in Attachment 2Q12 (CEII Appendix) and the Electrical Area Class drawings, provided in the supplemental response to the January 2, 2020 Data Request Q112 (CEII Appendix), filed on June 4, 2021. | Hazard Analysis Report in Appendix 13.H.3.
17. 6/4/2021 | N/A | Docket | 2020-06-05 | [6 empty] | Firewater Systems | 2021-06-04 | 41 | Numerous In response to item 129, Commonwealth provided the piping material specification for the firewater system. a. This pipe spec shows HDPE for piping, but also shows stainless steel for underground firewater risers. Confirm the intention to use stainless steel as underground firewater risers. b. In response to item 129, Commonwealth LNG confirmed the firewater ring would be 24- inch diameter. The updated piping specification provided in response to items 128 and 129 show the maximum allowable working pressure for 24-inch piping. The Firewater Demand Calculation (Doc. No. 078051C-000-CN-1930-0001, Appendix 13.S.10) shows the pump discharge pressure in Table 5. This pump discharge pressure would be greater than the maximum allowable working pressure of the HDPE piping. Confirm the piping material selection for the firewater system. Also confirm the maximum pressure requirement for the firewater system and demonstrate there would be adequate margin between the firewater system operating pressure and the maximum allowable piping pressure. |  |  |  |  | CPL Response Filed July 6, 2020: a. The firewater risers will not be stainless steel. The piping material specification will be updated and resubmitted as engineering progresses. b. The firewater pressure concern will be addressed as engineering progresses. Supplemental Response: Stainless steel was initially utilized for corrosion resistance due to seawater being used for the firewater system. Ductile iron with ceramic coat lining has shown to be acceptable for seawater service and may be substituted in lieu of stainless steel for the firewater risers. Currently there is no concern related to the fire water system pressure based on the preliminary fire water system evaluation. HDPE firewater piping, specification 1PD0H10, is only utilized underground, therefore the HDPE pipe will not be exposed to any of the higher temperatures that limit the MAWP. The underground HDPE firewater piping will be suitable for the firewater system pressure of 150 psi. Any concerns will be addressed during detailed engineering when a fire water system hydraulic model is developed. | The Firewater Demand Calculation Appendix 13.S.10 | 078051C-000-CN-1930-0001
18. 6/4/2021 | N/A | Docket | 2020-06-05 | [7 empty] | 2021-06-04 | 41 | Resource Report 13, Appendix 13.G.6 states that structures above 200’ would be submitted to the FAA for letters of hazard determination, table 4 lists 3 permanent structures that would meet this criteria as well as temporary construction cranes which would be taller than the permanent structures. However, the FAA determination letters filed on February 4, 2020 (Attachment Q209) are only for the permanent structures and say that construction equipment which is taller would require a separate notice to the FAA. Indicate the projected heights of construction equipment, such as cranes, and explain if notice has been given to the FAA for the construction equipment that would exceed the permanent structures in height. |  |  |  |  | During construction, Commonwealth will adhere to 14 C.F.R. Part 77. Cranage over 200’ will require FAA notification 45 days prior to erection.
5. 11/8/2021 | N/A | Docket | 2021-10-19 | [6 empty] | Process Design | 2021-11-08 | 41 | Updated cause and effect matrices were filed on June 4, 2021 in response to item 2 of FERC staff’s January 2, 2020 data request. The tagging on revised cause and effect (C&E) matrices now matches the Piping and Instrumentation Diagram (P&ID) tagging. Upon reviewing the C&E matrices, a number of equipment shutdowns are tied to a single instrument reading. For example, the Unit A11 C&E shows a shutdown of the mixed refrigerant (MR) compressor initiated by a high-high discharge pressure signal on the 1st stage MR compressor initiated by a single pressure transmitter, PIT-A11123. Similarly, this C&E matrix shows a number of single instrument readings initiating shutdowns of the MR compressor. The Instrumentation and Control Standard (15803-TS-0000-007) filed in Appendix 13.B states in section 4.2 that the SIS system would be designed to eliminate single point failures and would incorporate redundancy techniques. Therefore, provide responses to the following: a. Explain how and when redundant instrumentation and voting logic would be used to initiate trips and shutdowns. b. Explain if all of those instances are reflected in the submitted C&E matrices. |  |  |  |  | a. Instead of specifying SIS instrumentation with 2 out of 3 voting at this stage, the HAZOP and LOPA analysis for the facility will be performed first to ensure that proper safety targets are achieved. The process of this exercise will determine the levels of protection and redundancy needed for each Safety Instrumented Function (SIF). The HAZOP and LOPA activities will be performed during final design, and the requirements of the Instrumentation and Control Standard (15803-TS-0000-007) will be systematically applied. Current PID and C&E deliverables are still preliminary and will require further development in the next phase of the project. By using the HAZOP and LOPA process along with the Instrumentation and Control Standard as the design develops, consistency across the project and all impacted deliverables will be achieved. b. The submitted Cause & Effect matrices only show examples of 2 out of 3 voting as defined on the submitted P&IDs. All instances of required redundancy will be reflected on the C&E diagrams during final design when the P&IDs have been finalized, and as HAZOP/LOPA drive the design to implement the proper level of voting logic to achieve project safety targets. | Instrumentation and Control Standard Appendix 13.B | 15803-TS-0000-007
23. 11/8/2021 | N/A | Docket | 2021-10-19 | [6 empty] | Spacing & Plant Layout | 2021-11-08 | 41 | In response to several questions regarding high heat flux on equipment from impoundment fires, Commonwealth provided a document “Thermal Radiation from Pool Fires” (03601-RP-004) in the June 2021 filing. Figure 3-2 shows a high heat flux from the diesel storage impoundment overlaps one liquefaction block when using LNGFIRE3, while section 4.4 shows lower, non-concerning heat flux with the FDS modeling. However, there is equipment other than the liquefaction trains which could be impacted by high heat flux, such as the instrument air receivers (which provide air for safe shutdowns) as well as the liquid nitrogen storge vessel. Therefore, provide responses to the following: a. Demonstrate a fire from the diesel impoundment would not cause the instrument air receivers to lose functionality to provide the instrument air for a safe shutdown (i.e., structural failure, overpressure, Pressure Safety Valve (PSV) lift). b. Demonstrate the liquid nitrogen storage tank would not experience a BLEVE from a diesel storage impoundment fire. c. If cooling water from monitors is intended to provide the high heat flux mitigation for the instrument air receivers and liquid nitrogen storage tank, explain if there would be adequate visibility through the diesel fire soot cloud to allow first responders to focus the firewater on those vessels. |  |  |  |  | Diesel Fuel Storage Tank (T-4031) at 70⁰F operating temperature and Diesel Fuel Transfer Pumps (P-4032A/B) at 60 GPM (below 250 GPM) are rated as a low fire potential risk. This is due to diesel having a high flash point, above 125⁰F at atmospheric pressure and the pumps operating at intermittent and low flow rates even though diesel is a combustible liquid. An adjacent equipment fire scenario could cascade and impact the diesel storage with high heat flux, however that scenario, provided in the Thermal Radiation from Pool Fires (03601-RP-004), does not account for the layers of protection on the adjacent sources. The risk of fire scenario decreases once the fire protection related safeguards are considered. Control and extinguishing media for diesel fires are dry chemical extinguisher, fire monitors, hose stream, or low expansion foam monitors as applicable. As noted in response Q08, flame detection will be added to this area. a. Fire water monitors and hose streams can provide cooling on the instrument air receivers and foam monitors reduce the exposure risk from the diesel fire, together reducing the risk of compromising instrument air operation. Shutdown systems in the plant will be designed with a fail-to-safe philosophy with valves equipped with a spring return actuator and/or a local air volume tank. Fail-to-safe requirements will be further evaluated during HAZOP and LOPA analysis for the facility in final design. b. Fire water monitors and hose streams can provide cooling on liquid nitrogen storage tank and foam monitors reduce the exposure risk from the diesel fire, together reducing risk of BLEVE. Relief valves, rupture disks, and insulation that provide protection of the liquid nitrogen storage tank will be included, as required, when the design of the tank is finalized during final design. c. Water and Foam Monitors and hose streams will be utilized for equipment cooling of the nitrogen storage tanks and instrument air receivers. Firefighters will understand the layout of the equipment, understand the resources to be utilized, and be trained for firefighting this scenario. This area of the facility has multiple access paths to allow hose streams to be positioned from a safe location to cool equipment or extinguish the fire. The foam monitors will be pre-aimed at the diesel equipment to provide extinguishment of the diesel fire. Location of foam and water monitors will be optimized for access and visibility to address diesel fire scenarios in final design. | Thermal Radiation from Pool Fires | 03601-RP-004
27. 11/8/2021 | N/A | Docket | 2021-10-19 | [6 empty] | Spacing & Plant Layout | 2021-11-08 | 41 | Appendix 13.M.6, Buildings and Structures List (CLNG-LB-00-001), filed on August 20, 2019, section 2.4, provides that operator shelters would be installed inside the production facility and the number and location would be determined based on maintenance functional requirements, gas release, and blast studies. Provide a preliminary number and approximate locations for the operator shelters have been identified or indicate whether the number and locations of operator shelters would be determined in final design. |  |  |  |  | The number and location of operator shelters will be determined during final design based on the criteria identified. In addition, escape ladders will be provided from each level of the modules in the LNG trains, following OSHA codes the maximum travel distance to any ladder or stair will be no longer than 75 ft. Shelters will likely be located at the north end of trains of trains A, B, & C and the south end of trains D, E, & F, this will be confirmed during detailed design. | Buildings and Structures List | CLNG-LB-00-001
28. 11/8/2021 | N/A | Docket | 2021-10-19 | [6 empty] | Mechanical Design | 2021-11-08 | 41 | NFPA 59A stipulates the LNG storage tank top spill collection downcomer size must consider vaporization rates. Calculations in Appendix 13.S.3 assume the downcomer size must be doubled to account for vaporization but does not justify this assumption. Provide further analysis which validates the assumption doubling the pipe size would provide adequate capacity considering vaporization within the downcomer, or explain if a further analysis is planned for detailed design. |  |  |  |  | Downcomer sizing, which considers vaporization within the pipe, will be completed during final design. | Appendix 13.S.3
29. 11/8/2021 | N/A | Docket | 2021-10-19 | [6 empty] | Mechanical Design | 2021-11-08 | 41 | The modular design of the Commonwealth liquefaction and pretreatment modules would result in field connections between Balance of Plant Piping (BOP) and module terminal points. The location of the on-module terminal points would depend on both the manufacturing tolerance of the modules, as well as the tolerance placing the modules on their foundations. a. Explain what entity in the construction process would have ownership and responsibility for connecting the BOP piping to the module terminal points, while ensuring the interconnecting piping remains within allowable stress tolerances. b. Explain how the connections between the pretreatment and liquefaction modules would be made (i.e., would liquefaction module terminal points connect directly to the pretreatment module terminal points, or would there be interconnecting piping?). |  |  |  |  | a. During the construction process, the site construction contractor will have ownership and responsibility for connecting the BOP piping to the module terminal points. Connection point tolerances should be within normal construction acceptable limits, will be defined by construction and supplied to the module fabricator. Confirmation that the module as-built condition is within these tolerances will be made by a dedicated Dimension Control Contractor. Allowable stress for these connections will be evaluated and confirmed by the Engineering contractor. b. Connections between the Pretreatment and Liquefaction Modules will use a Single Weld Hook Up strategy, with no interconnecting piping.
30. 11/8/2021 | N/A | Docket | 2021-10-19 | [6 empty] | Mechanical Design | 2021-11-08 | 41 | Modular design and construction of the LNG storage tanks would require safe transportation to the proposed site. Provide responses for the following: a. Indicate what entity would be responsible for ensuring safe transportation of the modular receiving/inspecting the tanks, and placement on its’ foundation. b. Indicate where would the tanks be fabricated, and what entity would fabricate the tanks. c. Indicate what entity would be responsible for the foundation installation and outer containment tank installation. d. Explain what entity would be responsible for the QA/QC of the tanks (i.e., vendor, owner, EPC). |  |  |  |  | a. Bay Ltd, of 1414 Valero Way, Corpus Christi, TX 78409 will supply the completed tank as a Vendor supplied tagged equipment item. Bay will organize the tank transportation of the pre-fabricated component from their fabrication yard location to site. b. Fabrication yards in Corpus Christie and Morgan City are expected to be used, with some sub-assemblies fabricated in Mexico. A combination of in-house equipment and specialist sub-contractors will be used for the load-out, transportation, off-loading and emplacement. c. The foundation has two components, the piles and the reinforced concrete caps with pedestals. Morris-Shea Bridge Company Inc, of 609 South 20th Street Irondale, AL 35210 will install piles. The pile caps with pedestals will be constructed by a general contractor, who will be selected at a later date. The outer container tank installation would be by Bay Ltd, using a specialist sub-contractor, d. The tank will be supplied by Bay Ltd, who would be the responsible entity. The EPC Contractor will supply the (pre-installed) foundation and will ultimately be responsible for tank acceptance and function. The QA/QC will be a multi stage process, initially Bay Ltd will use their in-house QA/QC for fabrication and materials verification. The EPC contractor will also use their in-house QA/QC systems to verify that the work is complete in accordance with the Specifications and Contract. Such QA/QC will be done on an on-going process for review and acceptance. Further QA/QC and witnessing, will be done by the Owner’s Engineer at agreed acceptance hold points. Various specialist sub-contractors will be used for the load out, transportation, offloading, emplacement, and secondary container installation. These sub-contractors will have their own QA/QC processes, which will be included as part of the acceptance process. Note that the piling, pile caps, pedestals, haul roads, and offloading relieving platform will also be constructed by specialist sub-contractors. Sub-contractors for this work will have their own QA/QC processes, which will be included as part of the QA/QC acceptance process.
31. 11/8/2021 | N/A | Docket | 2021-10-19 | [6 empty] | Firewater Systems | 2021-11-08 | 41 | Firewater P&ID 078051C-000-PID-1931-0093, revision D (provided in the June 2021 filing) shows a large PSV in the flow path between the electric firewater pump (P-6002) and the main firewater ring. This configuration seems to be in error, typically firewater pump discharge PSVs are routed back to the firewater tank. Confirm the configuration for the pump discharge would be connected to the main firewater ring, and the discharge side PSV be connected to the firewater storage tank. |  |  |  |  | The Fire Water System P&ID 078051C-000-PID-1931-0093 will be updated during final design to depict the P-6002 pump discharge connected to the main fire water ring, and the discharge side of PSV connected to the fire water system storage tank. | Fire Water System P&ID | 078051C-000-PID-1931-0093, Rev D
32. 11/8/2021 | N/A | Docket | 2021-10-19 | [6 empty] | Firewater Systems | 2021-11-08 | 41 | The “Thermal Radiation from Pool Fires” analysis (03601-RP-004) demonstrates the high heat flux on the refrigerant storage vessels from a condensate storage dike fire. Other documentation provided in the June 2021 filing shows the refrigerant storage vessel deluge system is the only active protection system to reduce the risks to the refrigerant storage vessels from a condensate dike fire. a. Explain if foam generators would be effective at reducing the vaporization rate and/or intensity of a condensate dike fire. b. Explain why the condensate storage tank spill containment does not direct a spill to the S-4109 LNG Storage/Loading area impoundment like the nearby refrigerant storage vessels. c. Justify why passive protection methods for the refrigerant storge vessels have not been considered (i.e., firewalls, mounding, remote location, etc.). |  |  |  |  | a. Foam monitors utilizing low expansion foam will be used to extinguish and reduce the intensity of a condensate dike fire. These foam monitors will be added around the condensate storage and dike area and shown on the Fire Water System layouts in final design. High expansion foam is not recommended for condensate fires. b. Condensate should not spill directly into the LNG Storage/Loading Area impoundment (S-4109) because the hazard is handled differently from a mitigation/extinguishment as well as post scenario cleanup perspective. c. Alternate passive protection measures (i.e., firewalls, mounding, remote location, etc.) were considered during design development. Firewalls were not used due to concerns in restricting the ability to extinguish fire events. Mounding was not used because it would make leak detection less effective. Refrigerant vessels are currently located to minimize impact on surrounding equipment while following Subpart B siting requirements. d. Therefore, the Project determined deluge systems are the optimal arrangement to keep the refrigerant storage vessels cool. Passive fire protection on the equipment supports helps prevent escalation, and foam monitors reduce the exposure risk from the condensate fire. The area is protected with water and foam monitors, hose stream and dry chemical extinguishers allowing operations/firefighters to address the scenario as applicable. | Thermal Radiation from Pool Fires | 03601-RP-004
33. 11/8/2021 | N/A | Docket | 2021-10-19 | [6 empty] | Ignition Controls | 2021-11-08 | 41 | Updated Electrical Area Classification drawings were provided in the June 2021 filing. These electrical area classification drawings widely use API RP 500 figure 93 for the hazardous area around the liquefaction and pretreatment equipment. Figure 93 is reserved for Petroleum Pipeline Transportation Facilities, while API RP 500 figure 21 is reserved for Petroleum Refinery facilities. In response to item 109 of FERC Staff’s January 2020 data request, Commonwealth stated they would utilize API RP Figure 21, yet API RP 500 figure 93 is still being utilized. Clarify which area classification detail Commonwealth intends to utilize. |  |  |  |  | Commonwealth confirms that Figure 21 is the appropriate classification detail for this application. The drawings will be updated during final design to reflect this change.
Note on E2: Drew Jackson: number each request individually and maintain 1 per cell
Note on H2: Drew Jackson: Identify FERC Order Condition, planned IP Package or EIR related to request
Note on I2: Drew Jackson: This is the IP package that is the basis of the EIR

## Laws and Regulations (hidden)
Number` | CATEGORY | LAW / REGULATION including Guidelines | REFERENCE NUMBER | EFFECTIVE DATE | LOCAL LEGISLATION (if relevant) | GOVERNING BODY | SUMMARY OF LAW / REGULATION | RELEVANT SECTION(S) | RELEVANT FOR CONTRACTOR PERMITTING | SUBCONTRACTOR comments | DISCIPLINES
F-001 | Federal | Clean Air Act – Air Construction/Operating Permits | 42 U.S.C. §7401 et seq. | Current; site permit 03/28/2023 (mod 06/14/2024) | — | EPA / LDEQ | Regulates emissions (construction & ops), monitoring, and compliance for stationary sources. | Title V, PSD/NSR conditions | Yes | Coordinate equipment specs with permit limits. | Environmental, Process, Mechanical
F-002 | Federal | Clean Water Act – §401 Water Quality Certification | 33 U.S.C. §1341 | Current | — | LDEQ | State certification that federal permits meet state water quality standards. | WQC conditions | Yes | Implement WQC conditions in design & construction. | Environmental, Civil, Marine
F-003 | Federal | Clean Water Act – §404 Dredge/Fill Permits | 33 U.S.C. §1344; 33 CFR Parts 323, 325 | Current | — | USACE | Authorizes discharge of dredged/fill material into waters and wetlands. | Individual/PGP terms | Yes | Sequence in-water work with permit windows. | Environmental, Marine, Civil
F-004 | Federal | Coastal Zone Management Act Consistency | 16 U.S.C. §1456 | Current | Louisiana Coastal Zone Program | NOAA / LDNR | Requires federal actions/permits to be consistent with state coastal program. | §307 Consistency | Yes | Maintain consistency through design changes. | Environmental, Marine, Civil
F-005 | Federal | DOE Natural Gas Act – Export Authorization (FTA) | 15 U.S.C. §717b | 04/17/2020 (project auth date) | — | DOE/FE | Authorizes export of natural gas/LNG to FTA nations; terms remain in force. | DOE/FE Order terms | Yes | Track reporting and volume limits if applicable. | Commercial, Legal, Operations
F-006 | Federal | Endangered Species Act – USFWS | 16 U.S.C. §1531 et seq. | Current | — | USFWS | Consultation/terms to protect listed terrestrial/avian species. | §7 Consultation BO | Yes | Implement avoidance/mitigation measures. | Environmental, Construction
F-007 | Federal | Endangered Species Act – NMFS (Marine) | 16 U.S.C. §1531 et seq. | Current | — | NMFS | Marine species consultation & terms for in-water work. | §7 Consultation BO | Yes | Time-of-year restrictions, monitoring. | Environmental, Marine
F-008 | Federal | FAA Obstruction Evaluation/Determination of No Hazard | 14 CFR Part 77 | 02/21/2023 (DNH) | — | FAA | Evaluates structure heights/locations for airspace safety; sets marking/lighting. | Part 77 Subparts | Yes | Maintain as-approved heights/lighting. | Civil, Structural, Electrical
F-009 | Federal | FEMA Floodplain Map Revision – CLOMR/LOMR | 44 CFR Part 65 | Current | Cameron Parish Flood Ordinance | FEMA / Parish Floodplain Admin | Conditional and final map revisions for floodplain changes. | §§65.3–65.7; MT-2 | Yes | Prepare H&H models; align with Parish permit. | Civil, Hydrology, Survey, Environmental
F-010 | Federal | FERC – Natural Gas Act Section 3 Order (Authorization) | 15 U.S.C. §717b; 18 CFR Part 153 | 11/17/2022 (Authorization Order date) | — | FERC | Authorizes siting/construction; fixes code editions; includes 128 binding conditions. | Order & Conditions | Yes | Drive design/permits to Order requirements. | Project Management, All Disciplines
F-011 | Federal | Magnuson-Stevens – Essential Fish Habitat (EFH) | 16 U.S.C. §1801 et seq. | Current | — | NMFS | EFH consultation; implement conservation recommendations. | EFH response | Yes | Integrate measures in marine works. | Environmental, Marine
F-012 | Federal | Marine Mammal Protection Act – IHA | 16 U.S.C. §1361 et seq. | 03/06/2024 (IHA) | — | NMFS | Authorizes incidental harassment; requires monitoring/mitigation. | IHA conditions | Yes | Plan observers, shutdown zones. | Environmental, Marine
F-013 | Federal | National Historic Preservation Act – Section 106 | 54 U.S.C. §306108 | Current | — | SHPO/ACHP | Identify/evaluate effects on historic properties; mitigation/monitoring. | §106 MOA/letters | Yes | Protect cultural resources during work. | Environmental, Construction
F-014 | Federal | NEPA – FERC EIS & Mitigation Commitments | 42 U.S.C. §4321 et seq.; 18 CFR Part 380 | 09/09/2022 (FEIS) | — | FERC (lead) | Environmental review; mitigation measures incorporated into Order. | FEIS measures | Yes | Track in Implementation Plan. | Environmental, PM, Construction
F-015 | Federal | OSHA Process Safety Management (PSM) | 29 CFR 1910.119 | Current | — | OSHA | Management of hazards for highly hazardous chemicals; procedures/training/MOC. | All PSM elements | Yes | Align with PSSR, commissioning. | Process, Operations, HSE
F-016 | Federal | PHMSA – LNG Facility Safety Standards | 49 CFR Part 193 | Current | — | PHMSA | Federal safety standards for LNG design, siting, and operations. | Part 193 subparts | Yes | Coordinate LOD and design conformance. | Process, Mechanical, Civil, Safety
F-017 | Federal | Rivers & Harbors Act – Section 10 | 33 U.S.C. §403 | Current | — | USACE | Authorizes work in/over navigable waters (structures, dredging). | §10 permits | Yes | Coordinate with 404/408 sequencing. | Marine, Civil
F-018 | Federal | SPCC – Spill Prevention, Control & Countermeasure | 40 CFR Part 112 | Current | — | EPA | Prevents oil discharges; secondary containment & response planning. | Subparts A–C | Yes | Develop SPCC plan for oil-handling units. | Environmental, Mechanical, Civil
F-019 | Federal | USACE – Section 408 Permission | 33 U.S.C. §408 | 12/19/2022 (project) | — | USACE | Required for alterations to federal civil works (levees, channels). | 408 decision | Yes | Integrate conditions into design/construction. | Civil, Marine
F-020 | Federal | USCG Maritime Security – Facility Security | 33 CFR Part 105 | Current | — | USCG | Requires development, approval, and maintenance of a Facility Security Plan (FSP) and related security measures. | Subparts A–C | Yes | Coordinate FSP updates and drills with USCG. | Security, Marine, Operations
F-021 | Federal | USCG LNG Facilities – Waterfront Safety | 33 CFR Part 127 | Current | — | USCG | Safety and security standards for LNG facilities at the waterfront, including transfer and interface requirements. | 127.001–127.131 | Yes | Align marine/transfer design and procedures to Part 127. | Marine, Operations, Security
F-022 | Federal | EPA Risk Management Plan (RMP) | 40 CFR Part 68 | Current | — | EPA | Prevention and emergency response program for facilities with threshold quantities of regulated substances (flammables/toxics). | Subparts A–H | Yes | Confirm applicability; prepare/update RMP and coordinate with PSM. | HSE, Process, Operations
F-023 | Federal | EPCRA / SARA Title III (Emergency Planning & Community Right-to-Know) | 42 U.S.C. §11001 et seq.; 40 CFR Parts 355, 370, 372 | Current | — | EPA / State / Local LEPC | Chemical inventory notifications, emergency planning, Tier II, and TRI reporting as applicable. | §§302–312 (Tier II), §313 (TRI) | Yes | Establish chemical inventory and annual reporting workflow. | HSE, Operations, Legal
S-001 | State (LA) | LDNR Coastal Use Permit / Consistency | La. R.S. 49:214.30; LAC 43:I | 07/26/2024 (CUP) | Louisiana Coastal Zone | LDNR | State authorization for activities in the coastal zone. | CUP terms/conditions | Yes | Maintain conformance during changes. | Environmental, Marine, Civil
S-002 | State (LA) | LDEQ Air Permit (Title V/NSR/MACT/NSPS) | LAC 33:III | Current | — | LDEQ | Implements Clean Air Act at state level; construction & operation limits. | Permit conditions | Yes | Tie equipment specs to limits/monitoring. | Environmental, Process, Mechanical
S-003 | State (LA) | LDEQ LPDES – Hydrostatic/Vessel Testing | LAC 33:IX | Operations phase requirement upon issuance | — | LDEQ | Authorizes hydrotest/vessel testing discharges. | General Permit | Yes | Plan discharge timing & sampling. | Environmental, Mechanical
S-004 | State (LA) | LDEQ LPDES – Industrial Discharge | LAC 33:IX | Operations phase requirement upon issuance | — | LDEQ | Regulates process/utility discharges. | Individual Permit | Yes | O&M procedures and DMR reporting. | Environmental, Operations
S-005 | State (LA) | LDEQ LPDES – MSGP (Industrial Stormwater) | LAC 33:IX | Operations phase requirement upon Notice of Intent (NOI) | — | LDEQ | Industrial stormwater controls & monitoring; SWPPP. | Sector requirements | Yes | Implement BMPs & monitoring. | Environmental, Civil
S-006 | State (LA) | LDEQ LPDES – Sanitary Discharges | LAC 33:IX | Operations phase requirement upon issuance | — | LDEQ | Domestic/sanitary wastewater authorization. | General/Individual | Yes | Coordinate tie-in or onsite system. | Environmental, Utilities
S-007 | State (LA) | LDWF Threatened/Endangered Species | La. R.S. 56 | Various | — | LDWF | State-listed species coordination; avoidance/minimization. | Letters/conditions | Yes | Construction timing/techniques. | Environmental, Construction
S-008 | State (LA) | Louisiana DOTD Highway Access/Crossing | DOTD regs/policies | Prior to construction | — | La. DOTD | Permits for access drives and highway crossings. | Permit terms | Yes | Include HDD contingency planning. | Civil, Traffic, Construction
S-009 | State (LA) | Louisiana Office of State Lands – Water Bottoms Lease | La. R.S. 41:1701 et seq. | If required | — | LA Office of State Lands | Lease/rights to use state water bottoms. | Lease terms | Yes | Confirm footprint and need. | Legal, Marine
S-010 | State (LA) | CPRA – Coastal Protection & Restoration Authority Letter of No Impact | CPRA policy | Current | Louisiana Coastal Zone | CPRA | Confirms state-level coastal program has no objection/impact for proposed work. | LNO terms | Yes | Maintain alignment with LDNR CUP and project changes. | Environmental, Marine, Civil
S-011 | State (LA) | LDNR Coastal Use Permit – Geotechnical Investigation | LAC 43:I; permit-specific | 10/02/2023 (project example) | Louisiana Coastal Zone | LDNR | CUP specific to geotechnical investigations (borings, CPTs, etc.) within the coastal zone. | CUP conditions | Yes | Ensure geo works stay within authorized scope/season. | Geotechnical, Environmental
S-012 | State (LA) | LDWF Oyster Lease Consultation (State Leases) | La. R.S. 56; LDWF policy | Current | — | LDWF | Coordination to avoid/mitigate impacts to state oyster leases and reefs. | Consultation letters | Yes | Map lease footprints; agree on avoidance/mitigation. | Environmental, Marine
S-013 | State (LA) | LDEQ – Solid Waste Management (Construction/Demolition, Industrial) | LAC 33:VII | Current | — | LDEQ | Requirements for handling, storage, transport, and disposal of solid and C&D wastes. | Applicable Chapters of LAC 33:VII | Yes | Establish waste profiles and approved disposal sites. | Environmental, Construction
S-014 | State (LA) | LDEQ – Hazardous Waste Generator Requirements | LAC 33:V; 40 CFR Part 262 (incorporated) | Current | — | LDEQ | Generator classification, accumulation, labeling, training, and manifesting for hazardous wastes. | Generator standards & manifesting | Yes | Set up HW program; vendor and profiling controls. | Environmental, Operations
L-001 | Local (Cameron Parish) | Cameron Parish Coastal Use Permit / LONO | Parish policy | 07/06/2020 (example date) | Parish coastal policies | Cameron Parish | Local coastal authorization or no-objection. | LONO/CUP | Yes | Keep current with design updates. | Environmental, Marine
L-002 | Local (Cameron Parish) | Cameron Parish Floodplain Development Permit | Parish Flood Damage Prevention Ordinance | Prior to construction affecting SFHA | Flood Damage Prevention | Cameron Parish Police Jury | Permit for development in flood hazard areas; linked to FEMA CLOMR/LOMR. | Local permit requirements | Yes | Coordinate CLOMR/LOMR & deliverables. | Civil, Hydrology, Survey
L-003 | Local (Cameron Parish) | Cameron Parish Land Use / Zoning Designation | Parish ordinance | 09/08/2022 | Parish Land Use Map | Cameron Parish | Confirms LNG facility land-use compatibility. | Zoning designation | Yes | Ensure any changes stay compliant. | Legal, PM
L-004 | Local (Cameron Parish) | Parish Commercial/Development/Building Permits | Parish codes | As applicable | Building Code adoption | Cameron Parish | Local building/occupancy permits for permanent/temporary structures. | Permit/CO requirements | Yes | Align by discipline/scope. | Civil, Structural, Architectural
L-005 | Local (Cameron Parish) | Parish Driveway/Access (if required) | Parish policy | Prior to site use | — | Cameron Parish | Access connections to parish roads (if not under DOTD). | Driveway permit | Yes | Coordinate with traffic plan. | Civil, Construction
IS-001 | Industry Standard | ACI 376 – Concrete Structures for LNG Tanks | ACI 376-11 (2011) | 2011 | — | ACI | Design/analysis of concrete for full containment LNG tanks. | Key chapters 10.7.5, 10.8.4 | Yes | Coordinate with API tank standards. | Structural, Civil
IS-002 | Industry Standard | API 540 – Electrical Installations in Petroleum Facilities | API 540, 4th Ed. | 2016 | — | API | Electrical equipment/lighting practices in hazardous facilities. | Lighting/electrical specs | Yes | Coordinate with NEC/NFPA 70. | Electrical, I&C
IS-003 | Industry Standard | API 620 – Design & Construction of Large, Welded, Low-Pressure Tanks | API 620, 12th Ed. | Current | — | API | Governs low-pressure tanks (outer/ancillary where applicable). | Design/loads/testing | Yes | Tank vendor & civil integration. | Mechanical, Structural
IS-004 | Industry Standard | API 625 – Tank Systems for Refrigerated LNG Service | API 625, 1st Ed. | Current | — | API | System-level requirements for LNG storage tanks (integrates 620/650/ACI 376). | System integration | Yes | Drives holistic tank system design. | Mechanical, Structural, Civil
IS-005 | Industry Standard | API 650 – Welded Tanks for Oil Storage | API 650, 13th Ed. | Current | — | API | Fabrication/inspection of atmospheric tanks (non-LNG ancillary). | Fabrication/inspection | Yes | Ancillary tanks compliance. | Mechanical
IS-006 | Industry Standard | API 653 – Tank Inspection, Repair, Alteration, Reconstruction | API 653, 5th Ed. | Current | — | API | In-service inspection/repair for welded tanks. | Inspection intervals | Yes | Develop tank IM program. | Mechanical, Operations
IS-007 | Industry Standard | ASCE 24 – Flood Resistant Design and Construction | ASCE 24-14 | 2014 | — | ASCE | Flood-resistant requirements for structures/utilities. | Elevations, flood loads | Yes | Floodwall/grade design basis. | Civil, Structural
IS-008 | Industry Standard | ASCE 7 – Minimum Design Loads & Associated Criteria | ASCE 7-22 | 2022 | — | ASCE | Wind, seismic, flood, and other loads for structures. | Wind/seismic/flood | Yes | Basis for structural loading. | Structural, Civil
IS-009 | Industry Standard | ASME A13.1 – Pipe Labeling | ASME A13.1-2007 | 2007 | — | ASME | Identification of piping contents & flow direction. | Labeling scheme | Yes | Field labeling before service. | Mechanical, Operations
IS-010 | Industry Standard | ASME B31.3 – Process Piping | ASME B31.3-2016 | 2016 | — | ASME | Design/fab/inspection/testing of process piping. | Design/test chapters | Yes | Pressure/leak test plans. | Mechanical, Process
IS-011 | Industry Standard | ASME BPVC Section VIII – Pressure Vessels | ASME VIII-2017 | 2017 | — | ASME | Design/fabrication/testing of pressure vessels. | UG/Appendices | Yes | Commissioning test criteria. | Mechanical
IS-012 | Industry Standard | ASTM F2656 – Crash-Tested Vehicle Barriers | ASTM F2656-15 | 2015 | — | ASTM | Performance specs for anti-ram barriers at entrances. | Rating/impact levels | Yes | Select barrier type/speed. | Security, Civil
IS-013 | Industry Standard | ISA 18.2 – Alarm Management | ISA-18.2-2016 | 2016 | — | ISA | Alarm lifecycle management for control systems. | Philosophy/metrics/MOC | Yes | Reduce alarm flooding/complacency. | I&C, Operations
IS-014 | Industry Standard | ISA 84.00.07 – Hazard Detection (Performance) | ISA 84.00.07-2018 | 2018 | — | ISA | Methodology for detector coverage/performance justification. | Performance targets | Yes | Detector placement & voting logic. | I&C, Safety
IS-015 | Industry Standard | NFPA 10 – Portable Fire Extinguishers | NFPA 10-2018 | 2018 | — | NFPA | Extinguisher selection, spacing, and travel distances. | Spacing tables | Yes | Include in fire protection layout. | Fire Protection, HSE
IS-016 | Industry Standard | NFPA 22 – Water Tanks for Private Fire Protection | NFPA 22-2018 | 2018 | — | NFPA | Design & performance for firewater storage tanks. | Tank design/acceptance | Yes | Acceptance tests pre-fluids. | Fire Protection, Civil
IS-017 | Industry Standard | NFPA 59A – Production, Storage & Handling of LNG (Primary) | NFPA 59A-2019 | 2019 | — | NFPA | Primary LNG standard governing design, siting, operations. | Multiple topics per Order | Yes | Locked edition per FERC. | Process, Mechanical, Civil, Fire, I&C
IS-018 | Industry Standard | NFPA 59A – Legacy Provisions (Labeling/Interfaces) | NFPA 59A-2001 | 2001 | — | NFPA | Legacy requirements still invoked in specific areas. | Specific legacy refs | Yes | Apply only where cited. | Mechanical, Electrical
IS-019 | Industry Standard | NFPA 70 – National Electrical Code (NEC) | NFPA 70-2017 | 2017 | — | NFPA | Electrical safety & installation code for hazardous locations. | Articles 500-505 etc. | Yes | Area classification & wiring. | Electrical, I&C
IS-020 | Industry Standard | NFPA 497 – Classification of Flammable Gases/Vapors | NFPA 497-2017 | 2017 | — | NFPA | Guide for classifying hazardous (classified) locations. | Release rates/figures | Yes | Supports electrical area classification. | Electrical, I&C
IS-021 | Industry Standard | UL 1709 – Rapid Rise Fire Tests for Protection Materials | UL 1709, 6th Ed. | Current | — | UL | Fire exposure test for structural/critical systems survivability. | 20-minute exposure | Yes | Cable/tray/protection selection. | Fire Protection, Electrical, I&C
IS-022 | Industry Standard | IEEE 1584 – Arc-Flash Hazard Calculations (Best Practice) | IEEE 1584-2018 | 2018 | — | IEEE | Empirical model for arc-flash incident energy & PPE. | Method & tables | No | Not mandated by FERC; recommended for risk mitigation. | Electrical, HSE
IS-023 | Industry Standard | ISO 55001 – Asset Management (Best Practice) | ISO 55001:2014 | 2014 | — | ISO | Management system for lifecycle asset reliability. | Clauses 4–10 | No | Not mandated by FERC; recommended for risk mitigation. | Operations, Maintenance
IS-024 | Industry Standard | NFPA 70E – Electrical Safety in the Workplace (Best Practice) | NFPA 70E-2021 | 2021 | — | NFPA | Work practices & PPE to protect workers from electrical hazards. | Arc-flash boundaries/PPE | No | Not mandated by FERC; recommended for risk mitigation. | Electrical, HSE
IS-025 | Industry Standard | OSHA 1910 Subpart D/E – Walking-Working/Exit Routes (Best Practice) | 29 CFR 1910 Subparts D, E | Current | — | OSHA | Safe access/egress; complements alarm/evac planning. | Egress & signage | No | Not mandated by FERC; recommended for risk mitigation. | HSE, Facilities
IS-026 | Industry Standard | NFPA 850 – Fire Protection for Electric Generating Plants & High Voltage Substations | NFPA 850-2015 | 2015 | — | NFPA | Guidance for transformer fire protection and to prevent cascading damage (referenced for transformer spacing/walls). | Transformer fire protection | Yes | Apply to transformer yard design per FERC references. | Electrical, Fire Protection, Civil
IS-027 | Industry Standard | API RP 500 – Classification of Locations for Electrical Installations (Petroleum Facilities) | API RP 500, 3rd Ed. | 2012 | — | API | Guidance for hazardous (classified) locations used with NFPA 70/NFPA 497 (referenced for area classification figures). | Figures & classification methods | Yes | Support electrical area classification per FERC conditions. | Electrical, I&C
IS-028 | Industry Standard | NOAA Global & Regional Sea Level Rise Scenarios for the U.S. | NOAA Technical Report NOS CO-OPS 083 (Feb 2022) | 2022 | — | NOAA | Provides sea-level rise scenarios used to set design basis for floodwalls and elevations over facility life. | Intermediate curve selection | Yes | Basis for floodwall/elevation design inputs. | Civil, Structural, Coastal
IS-029 | Industry Standard | U.S. NRC Regulatory Guide 1.12 – Instrumentation for Earthquakes (Rev. 3) | NUREG/CR; RG 1.12 Rev. 3 | 1997 (Rev. 3) | — | U.S. NRC | Guidance for seismic instrumentation and strong-motion monitoring (invoked for tank/site seismic monitoring). | Sections 1, 3–9 | Yes | Define seismic monitoring system and alarm philosophy. | Structural, I&C, Seismic
IS-030 | Industry Standard | AIChE Guidelines for Analyzing & Managing the Security Vulnerabilities of Fixed Chemical Sites | AIChE CCPS (2003) | 2003 | — | AIChE/CCPS | Methodology for security vulnerability assessment supporting barrier selection and ratings. | SVA methodology | Yes | Supports selection of crash ratings and security design. | Security, Risk, Civil
IS-031 | Industry Standard | ASME B31.8 – Gas Transmission & Distribution Piping Systems | ASME B31.8 | Current | — | ASME | Design, construction, testing, and O&M for gas pipelines (for project pipeline segments as applicable). | Design/test/O&M | Yes | Apply to pipeline outside process scope as required. | Pipeline, Mechanical, Civil
IS-032 | Industry Standard | ASME B31.4 – Pipeline Transportation Systems for Liquids & Slurries | ASME B31.4 | Current | — | ASME | Design and operation of liquid hydrocarbon pipelines (if applicable to condensate/NGL service). | Design/test/O&M | Yes | Use where liquid pipelines are present. | Pipeline, Mechanical, Civil

## Contractor Permits Register (P) (hidden)
Permit ID | Category | Issuing Agency | Permit Description | Date Required or Received | Status | Periodic Reporting (Yes/No) | Frequency | Responsible Party | Date Submitted | Date Approved | Dependencies / Roadblocks | Risk Category | Potential Impact | Mitigation Measures | Contingency Plan | Notes
P-1 | Federal | FAA | Notice of Proposed Construction, 7460 forms & Determination of No Hazard, For all applicable temporary construction equipment, cranes, etc. | Prior to need | Not Started |  |  | Site Prep Sub |  |  | Crane mobilization schedule | Schedule Delay | Delay in crane use | Submit 30+ days in advance; pre-consult with FAA | Reschedule lifts or use lower equipment
P-2 | Federal | FCC | Radio Licenses (for radio use during construction) | Prior to need | Not Started |  |  | Site Prep Sub |  |  | Procurement of radios | Schedule Delay | Inability to communicate on site | Apply early; verify frequency availability | Use alternate comms (cell, satcom)
P-3 | Federal | EPA | Hazardous Waste Generator Identification Number and Permits required for the disposal of Hazardous Waste | Prior to need | Not Started | Yes | Biennial / Quarterly (depending on generator status) | Site Prep Sub |  |  | Waste stream identification | Environmental Non-Compliance | Fines; work stoppage | Identify waste streams early; secure hauler contracts | Store waste temporarily until approval
P-4 | Federal | USCG | Notice to Mariners - Dredging | Prior to Dredging activities | Not Started | Yes | As needed during dredging operations | Marine Sub / MOF Sub |  |  | Marine work scheduling | Schedule Delay | Delay in dredging | Submit 2+ weeks before dredging | Shift dredging to available clearance periods
P-5 | State | LDEQ – Water Quality Division | LAG780000 General Permit for Construction/Demolition and Wood Waste | Prior to need | Not Started | Yes | Annual or Quarterly | Site Prep Sub |  |  | Construction start date | Environmental Non-Compliance | Fines; stop work order | Submit early; ensure contractor compliance | Store waste until permit in place
P-6 | State | LDEQ | LAG56000 Sanitary Discharge Permit <25,000 gpd (or equivalent waste permit) | Prior to need | Not Started | Yes | Monthly | By sub permitting the associated structure |  |  | Utility connection availability | Schedule Delay | Unable to discharge sanitary waste | Apply early; coordinate with utility | Use portable facilities
P-7 | State | LDEQ | LAR100000 Storm Water Discharge Construction >5 acres | Prior to need | Not Started | Yes | Quarterly + Annual | Site Prep Sub |  |  | Site grading start | Environmental Non-Compliance | Fines; stop work order | Prepare SWPPP before site work | Hold grading until permit received
P-8 | State | LDEQ | Louisiana Pollutant Discharge Elimination System General Permit (LPDES) LAG670000 – Hydrostatic Test and Vessel Testing Wastewater | Prior to hydro test and vessel testing | Not Started | Yes | During discharge period (event-based) | P-8 – LNG Tank Sub |  |  | Test schedule delays | Schedule Delay | Unable to perform testing | Apply 45+ days prior | Contain testing water onsite
P-9 | State | LDEQ | Construction Spill Containment & Countermeasure Plan (SPCC) | Prior to need | Not Started | Yes | Annual + Immediate (if spill occurs) | Site Prep Sub |  |  | Hazard assessment | Environmental Non-Compliance | Spill fines; work stoppage | Develop SPCC before mobilization | Deploy spill kits/barriers
P-10 | State | LDWF | License to Dredge from State Water Bottoms | Prior to need | Not Started | Yes | Daily / Weekly during dredging | P-10 – Marine Sub / MOF Sub |  |  | Overlap with USCG requirements | Regulatory Delay | Dredging cannot start | Apply early; coordinate with USCG notice | Reschedule dredging
P-11 | State | LADOT | Temporary and Permanent Driveways and/or Access to the Site | Prior to need | Not Started |  |  | Site Prep Sub |  |  | Access road completion | Schedule Delay | Restricted site access | Apply early; coordinate with DOT traffic plan | Use alternate access
P-12 | Local | Cameron Parish Police Jury | Commercial / Development Permit | Prior to need | Not Started |  |  | Site Prep Sub |  |  | Local processing timelines | Schedule Delay | No work start without permit | Submit complete application early | Delay NTP until approval
P-13 | Local | Cameron Parish Police Jury | Building Occupancy Permit - Permanent - Buildings | Prior to occupancy | Not Started |  |  | By sub completing building scope |  |  | Completion of construction | Occupancy Delay | Unable to use building | Apply during final phase | Request temporary occupancy
P-14 | Local | Cameron Parish Police Jury | Building Occupancy Permit - Portable/Temporary Building Permits | Prior to occupancy | Not Started |  |  | By sub completing building scope |  |  | Facility delivery schedule | Occupancy Delay | Unable to use temporary structures | Apply before delivery | Use alternate facility
P-15 | Local | Cameron Parish Police Jury | Floodplain Development Permit, LOMR or CLOMR as needed) | NTP or prior to site work under an applicable LNTP | In-Process | Yes | Event-based during construction | LEI |  |  | FEMA mapping delays | Regulatory Delay | Site work stoppage | Submit LOMR early; coordinate with FEMA | Delay site work start
P-16 | Other | Cameron Parish Fire Marshall | Fire Protection | Prior to need | Not Started |  |  | By subs installing firewater systems |  |  | Final design readiness | Life Safety Risk | Unable to operate facility | Submit early; pre-approval before install | Deploy temporary fire suppression
P-17 | Other | LDEQ | Temporary Water (if required) | Prior to need | Not Started | Yes | Daily / Weekly during use | By sub withdrawing or obtaining temporary water |  |  | Water source availability | Schedule Delay | Unable to complete work | Apply early; secure alternate source | Use water trucks/storage tanks
P-18 | Other | LADOT/ DOT | All transportation approvals | Prior to use of roadways or rail as applicable | Not Started | Yes | As needed during transport operations | TRC / Construction |  |  | Delivery schedule coordinatio | Schedule Delay | Equipment/material delays | Submit early; stagger deliveries | Use alternate transport routes

## Operator Permits (Q) (hidden)
Permit ID | Category | Issuing Agency | Permit Description | Date Required or Received | Status | Periodic Reporting (Yes/No) | Frequency | Responsible Party | Date Submitted | Date Approved | Dependencies / Roadblocks | Risk Category | Potential Impact | Mitigation Measures | Contingency Plan | Notes
Q-1 | Federal | Federal Energy Regulatory Commission (FERC) | FERC Section 3 Order | 2022-11-17 | In Good Standing |  |  | Regulatory Affairs |  |  | N/A | Regulatory Non-Compliance | Loss of federal authorization; project shutdown | Monitor FERC docket; maintain compliance documentation | Pause related construction until FERC issues updated order
Q-1 | Federal | Federal Energy Regulatory Commission (FERC) | FERC Notice to Proceed (NTP) | Prior to any work on Site | Not Started |  |  | Regulatory Affairs |  |  | FERC review and approval before site work | Schedule Delay | Delay to site mobilization and start of work | Prepare and submit complete NTP package early; track review | Adjust mobilization schedule; reallocate crews to other work areas
Q-2 | Federal | US Army Corps of Engineers (USACE) | Clean Water Act Sec. 404 / Rivers & Harbors Act Sec. 10 | NTP or earlier prior to working under an applicable LNTP | Not Started |  |  | Environmental / Permitting |  |  | Coordination with USACE review schedule | Regulatory Non-Compliance | Inability to conduct in-water work; potential fines | Engage USACE early; submit complete application with all required studies | Shift construction sequencing to non-jurisdictional areas | application meeting with USACE
Q-3 | Federal | US Army Corps of Engineers (USACE) | Section 408 (Rivers & Harbors Act Sec. 14) | 2022-12-19 | In Good Standing |  |  | Environmental / Permitting |  |  | N/A | Regulatory Non-Compliance | Work stoppage on USACE jurisdictional activities | Coordinate with USACE reviewer and stakeholders ahead of deadlines | Reschedule work requiring USACE approval to later phase
Q-4 | Federal | US Army Corps of Engineers (USACE) | Programmatic General Permit – Category 1 (Geotechnical) | 2021-03-04 | In Good Standing |  |  | Environmental / Permitting |  |  | N/A | Schedule Delay | Delay to geotechnical or construction activities | Submit early to allow processing time before geotechnical work | Reassign geotechnical work to permitted locations
Q-5 | Federal | US Coast Guard (USCG) | Channel Marker Relocation Approval | 2021-10-18 | In Good Standing |  |  | Marine Operations |  |  | N/A | Regulatory Non-Compliance | Navigation hazards; inability to relocate markers | Coordinate with USCG; schedule relocation well in advance | Delay or reroute marine operations until approval obtained
Q-6 | Federal | Federal Aviation Administration (FAA) | FAA Notice of Proposed Construction – Permanent Structures | 2023-02-21 | In Good Standing |  |  | Construction / Engineering |  |  | N/A | Schedule Delay | Delay in construction involving tall structures | File FAA application 30+ days before need; verify equipment heights | Reschedule lifts; use alternate equipment or lower heights
Q-7 | Federal | US Fish & Wildlife Service (FWS) | Special Use Permit (SUP) | 2024-07-16 | In Good Standing |  |  | Environmental / Permitting |  |  | N/A | Environmental Impact | Suspension of permitted activities; environmental enforcement | Apply early with complete SUP package; maintain habitat compliance | Postpone activities impacting habitat until SUP granted
Q-8 | State | Department of Natural Resources (LDNR), Office of Coastal Management (OCM) | Coastal Use Permit / CZMA Consistency | 2024-07-26 | In Good Standing |  |  | Environmental / Permitting |  |  | N/A | Environmental Impact | Inability to perform coastal work; federal consistency issues | Submit CZMA package early; coordinate with LDNR-OCM | Reschedule coastal work; focus on upland activities
Q-9 | State | LDNR Office of Coastal Management (OCM) | Coastal Use Permit – Geotechnical Investigation | 2023-10-02 | In Good Standing |  |  | Environmental / Permitting |  |  | N/A | Environmental Impact | Delay to geotechnical field work | Pre-schedule geotechnical activities to align with permit timing | Delay geotechnical work until permit received
Q-10 | State | Louisiana Department of Environmental Quality (LDEQ) – Water Quality Division | LPDES Permit LAG670000 – Hydrostatic & Vessel Testing Wastewater | Prior to Operations | Not Started | Yes | Per discharge event during operations | Environmental Compliance (Water Quality) |  |  | Operational readiness; discharge plan completion | Regulatory Non-Compliance | Prohibited hydrostatic/vessel testing; operational delays | Prepare discharge plan; submit LPDES application early | Use containment tanks for hydro/vessel testing water | Use containment tanks until approved
Q-11 | State | LDEQ – Water Quality Division | LPDES Permit LAR050000 – Multi Sector Stormwater | Prior to Operations | Not Started | Yes | Quarterly & Annual | Environmental Compliance (Water Quality) |  |  | Stormwater system readiness; SWPPP completion | Environmental Impact | Stormwater discharge violations; environmental enforcement | Develop SWPPP; submit stormwater permit application in advance | Install temporary stormwater controls until permit issued | Install temporary stormwater controls
Q-12 | State | LDEQ – Water Quality Division | LPDES LAG53000 & LAG570000 – Sanitary Discharges | Prior to Operations | Not Started | Yes | Quarterly & Annual | Environmental Compliance (Water Quality) |  |  | Utility connection and sanitary infrastructure completion | Schedule Delay | Inability to discharge sanitary waste; work disruption | Coordinate with utility provider for sanitary connections | Deploy portable sanitary facilities until connection approved
Q-13 | State | LDEQ – Water Quality Division | LPDES Industrial Discharge Permit | Prior to Operations | Not Started | Yes | As specified in permit | Environmental Compliance (Water Quality) |  |  | Industrial discharge infrastructure readiness | Regulatory Non-Compliance | Violation of discharge limits; potential fines | Verify effluent standards; prepare complete industrial permit package | Store effluent temporarily; suspend related operations | Hold operations until approval
Q-14 | State | LDEQ – Air Quality Division | Air Emissions Permit (Title V & PSD) – Mod 6/14/24 | 28-Mar-23 (Permit Mod 6/14/24) | In Good Standing | Yes | Semi-annual & Annual | Environmental Compliance (Air Quality) |  |  | N/A | Regulatory Non-Compliance | Air quality violations; operational restrictions | Track air permit renewal/mod requirements; coordinate with LDEQ | Adjust operations to meet existing air permit limits
Q-15 | State | Louisiana Office of State Lands | State Water Bottoms Lease (if required) | Prior to dredging activities | Not Started |  |  | Land Management |  |  | Coordination with Louisiana Office of State Lands | Schedule Delay | Delay in dredging or marine work | Start lease process early; confirm state land ownership | Delay dredging until lease secured; adjust marine schedule
Q-16 | Federal | Federal Energy Regulatory Commission (FERC) | Final Environmental Impact Statement (FEIS) | 2022-09-09 | In Good Standing |  |  | Regulatory Affairs |  |  | N/A | Regulatory Non-Compliance | Loss of environmental approval; regulatory hold | Maintain FEIS compliance; monitor for supplemental review needs | Pause activities requiring FEIS compliance until resolved
Q-17 | Federal | US Department of Energy (DOE) | NGA Section 3 – FTA / Non FTA Authorization | FID | In Good Standing |  |  | Regulatory Affairs |  |  | N/A | Regulatory Non-Compliance | Inability to export LNG; loss of market access | Engage DOE early; prepare export compliance documentation | Delay LNG export operations; redirect capacity if possible
Q-18 | Federal | US Coast Guard (USCG) | USCG Letter of Recommendation | 2019-03-07 | Needs Verification |  |  | Marine Operations |  |  | Age of existing permit; USCG confirmation | Regulatory Non-Compliance | Invalidation of USCG endorsement; marine operation halt | Confirm renewal needs with USCG; submit in advance if required | Suspend marine operations until USCG authorization renewed | Permit may be expired
Q-18 | Federal | US Coast Guard (USCG) | Annual Water Suitability Assessment (WSA) | 2024-03-25 | In Good Standing | Yes | Annual | Marine Operations |  |  | N/A | Regulatory Non-Compliance | Loss of WSA approval; marine operation restrictions | Schedule WSA update with USCG; maintain operational logs | Restrict operations in waterways until WSA approval obtained
Q-19 | Federal | US Coast Guard (USCG) | Facility Security Plan / Marine Ops Manual / Emergency Response Plan | Prior to introduction of hydrocarbons | Not Started | Yes | Annual review/update or after major changes | Marine Operations / HSE |  |  | Coordination with USCG security plan review | Health & Safety Risk | Inability to begin operations; safety enforcement action | Submit all security/emergency manuals 60+ days before operations | Operate under interim safety/emergency procedures
Q-20 | Federal | US Fish & Wildlife Service (FWS) | ESA Sec. 7 & Biological Opinion; MBTA; BGEPA | N/A | In Good Standing | Yes | As required by ESA/MBTA/BGEPA conditions | Environmental / Permitting |  |  | N/A | Environmental Impact | Environmental enforcement; endangered species work halt | Coordinate with FWS for ESA compliance; update BUDM as needed | Suspend species-impacting work until clearances restored
Q-21 | Federal | U.S. Dept of Transportation | ESA Sec. 7 (NMFS) | 2023-06-27 | In Good Standing |  |  | Construction Management |  |  | N/A | Schedule Delay | Delay to construction requiring DOT notification | Submit DOT notice per schedule; confirm project milestones | Postpone DOT-covered activities until notice is accepted
Q-22 | Federal | National Marine Fisheries Services (NMFS) PRD | Magnuson Stevens EFH Consultation | N/A | In Good Standing | Yes | As required by ESA conditions | Environmental / Permitting |  |  | N/A | Environmental Impact | Loss of ESA clearance; work stoppage | Coordinate with NMFS PRD; provide required biological assessments | Suspend ESA-sensitive work; adjust to unaffected areas
Q-23 | Federal | NMFS Habitat Conservation Division | Marine Mammal Protection Act – Incidental Harassment Auth. (IHA) | 2022-11-22 | In Good Standing |  |  | Environmental / Permitting |  |  | N/A | Environmental Impact | Loss of EFH approval; work stoppage | Prepare EFH documentation; coordinate with NMFS Habitat Division | Postpone EFH-impacting work until consultation complete
Q-24 | Federal | NMFS Office of Protected Resources | PHMSA Hazard Analysis Review & Letter of Determination | 2024-03-06 | In Good Standing | Yes | As required in IHA (varies; often annual) | Environmental / Permitting |  |  | N/A | Environmental Impact | Marine mammal protection violations; fines | File IHA application well in advance; address public comments | Suspend marine mammal-impacting operations
Q-25 | Federal | Pipeline and Hazardous Materials Safety Administration (PHMSA) | Section 106 Consultation (NHPA) | N/A | In Good Standing | Yes | As required in PHMSA Letter of Determination | Pipeline Safety / Regulatory |  |  | N/A | Regulatory Non-Compliance | PHMSA non-compliance; operational restrictions | Maintain PHMSA compliance; update hazard analysis if needed | Delay pipeline commissioning until PHMSA issues approval
Q-26 | State | Louisiana State Historic Preservation Office (SHPO) | Threatened & Endangered Species Consultation | N/A | In Good Standing |  |  | Cultural Resources / Environmental |  |  | N/A | Regulatory Non-Compliance | Loss of cultural resource clearance; work stoppage | Coordinate SHPO consultation; maintain cultural monitoring as required | Suspend construction in affected areas until SHPO clearance
Q-27 | State | Louisiana Department of Wildlife and Fisheries (LDWF) | Oyster Lease Consultation | 2020-06-04 | In Good Standing |  |  | Environmental / Permitting |  |  | N/A | Environmental Impact | Endangered species violations; fines | Coordinate with LDWF; incorporate species avoidance measures | Postpone work impacting protected species
Q-28 | State | Louisiana Department of Wildlife and Fisheries (LDWF) | Section 401 Water Quality Certification | 2021-12-07 | In Good Standing |  |  | Environmental / Permitting |  |  | N/A | Environmental Impact | Delay to marine activities; oyster lease conflicts | Coordinate with LDWF; review oyster lease maps and boundaries | Avoid oyster lease areas; modify work footprint
Q-29 | State | LDEQ – Water Quality Division | Highway Crossing Permit – Feed Gas Pipeline | N/A | In Good Standing | Yes | As specified in WQC (may include annual) | Environmental Compliance (Water Quality) |  |  | N/A | Regulatory Non-Compliance | Loss of water quality certification; work stoppage | Prepare application early; address water quality issues proactively | Delay discharge activities until certification secured
Q-30 | State | Louisiana Department of Transportation (LADOT) | Coastal Use Permit / Letter of No Objection | Prior to Pipeline Construction | In Good Standing |  |  | Construction Management |  |  | N/A | Schedule Delay | Delay to pipeline construction; DOT non-compliance | Coordinate with LADOT; finalize crossing design early | Delay pipeline work; reroute if possible
Q-31 | Local | Cameron Parish Police Jury | Land Use Designation (No Zoning) | 2020-07-06 | Needs Verification |  |  | Environmental / Permitting |  |  | Cameron Parish review and approval process | Regulatory Non-Compliance | Loss of local approval; work stoppage | Submit complete parish permit package early; confirm requirements | Delay parish-covered work until permit reissued | Permit may be expired
Q-32 | Local | Cameron Parish Police Jury | Letter of No Impact | 2022-09-08 | In Good Standing |  |  | Environmental / Permitting |  |  | N/A | Regulatory Non-Compliance | Restrictions on land use; local enforcement | Maintain parish land use compliance documentation | Restrict land use to allowable activities until compliance regained
Q-33 | Local | Coastal Protection and Restoration Authority (CPRA) |  | 2019-08-28 | Needs Verification |  |  | Environmental / Permitting |  |  | CPRA review and letter issuance | Regulatory Non-Compliance | Loss of CPRA clearance; coastal work stoppage | Submit CPRA package early; coordinate with reviewers | Delay CPRA-regulated coastal work until clearance secured | Permit may be expired

## Acronym Index (hidden)
Acronym | Full Name / Definition
ACI | American Concrete Institute
AIChE | American Institute of Chemical Engineers
API | American Petroleum Institute
ASCE | American Society of Civil Engineers
ASME | American Society of Mechanical Engineers
ASTM | ASTM International (formerly American Society for Testing and Materials)
BPVC | Boiler and Pressure Vessel Code
BO | Biological Opinion
C&D | Construction and Demolition
CFR | Code of Federal Regulations
CLOMR | Conditional Letter of Map Revision
CO | Certificate of Occupancy
CPRA | Coastal Protection and Restoration Authority
CPT | Cone Penetration Test
CUP | Coastal Use Permit
DNH | Determination of No Hazard
DOE | Department of Energy
DOT | Department of Transportation
DOTD | Department of Transportation and Development (Louisiana)
EFH | Essential Fish Habitat
EIS | Environmental Impact Statement
EPA | Environmental Protection Agency
EPCRA | Emergency Planning and Community Right to Know Act
FEMA | Federal Emergency Management Agency
FERC | Federal Energy Regulatory Commission
FEIS | Final Environmental Impact Statement
FE | Fossil Energy (DOE Office of Fossil Energy)
FTA | Free Trade Agreement
HDD | Horizontal Directional Drilling
H&H | Hydrology and Hydraulics
HSE | Health, Safety, and Environment
HW | Hazardous Waste
I&C | Instrumentation and Control
IHA | Incidental Harassment Authorization
IM | Integrity Management
ISA | International Society of Automation
ISO | International Organization for Standardization
LDNR | Louisiana Department of Natural Resources
LDEQ | Louisiana Department of Environmental Quality
LDWF | Louisiana Department of Wildlife and Fisheries
LDOT | Louisiana Department of Transportation
LEPC | Local Emergency Planning Committee
LNG | Liquefied Natural Gas
LNO | Letter of No Objection
LOMR | Letter of Map Revision
LOD | Level of Detail
LPDES | Louisiana Pollutant Discharge Elimination System
MACT | Maximum Achievable Control Technology
MOC | Management of Change
MOA | Memorandum of Agreement
MSGP | Multi Sector General Permit
MT-2 | FEMA MT 2 Flood Map Revision Application
NEC | National Electrical Code
NEPA | National Environmental Policy Act
NFPA | National Fire Protection Association
NMFS | National Marine Fisheries Service
NOAA | National Oceanic and Atmospheric Administration
NOI | Notice of Intent
NPS | New Source Performance Standards
NRC | Nuclear Regulatory Commission
NSA | Noise Source Assesment
NSR | New Source Review
O&M | Operations and Maintenance
OSHA | Occupational Safety and Health Administration
PGP | Programmatic General Permit
PHMSA | Pipeline and Hazardous Materials Safety Administration
PM | Project Management
PPE | Personal Protective Equipment
P&ID | Piping and Instrumentation Diagram
PFD | Process Flow Diagram
PSM | Process Safety Management
PSD | Prevention of Significant Deterioration
PSSR | Pre-Startup Safety Review
RG | Regulatory Guide
RMP | Risk Management Plan
R.S. | Revised Statutes (Louisiana)
SARA | Superfund Amendments and Reauthorization Act
SFHA | Special Flood Hazard Area
SHPO | State Historic Preservation Officer
SPCC | Spill Prevention, Control, and Countermeasure
SVA | Security Vulnerability Assessment
SWPPP | Stormwater Pollution Prevention Plan
TRI | Toxics Release Inventory
UL | Underwriters Laboratories
USACE | United States Army Corps of Engineers
USCG | United States Coast Guard
USFWS | United States Fish and Wildlife Service
Sector General Permit
Startup Safety Review